## Changelog
Date | Version | User | Changes | Remarks
2025-08-23 | 0.1 | M Buss | Structural changes for Oe Model management.
2025-12-31 | 0.5 | M Buss | object modelling definition complete including security modelling. | Outstanding are discussions regarding the Security Officer Role, its duties and scope. To be done - remove objects that were proposed but are now not needed, remove tabs marked ToDelete, clarify the Security issues and assumptions.
2026-01-19 | 0.5.1 | M Buss | Removal of Comms Module identity and object modelling. Addition of Key management for all AAs to Security Officer Role
2026-03-16 | 0.6 | M Buss | Clean version after review cycle
2026-04-17 |  | M Buss | Redacted version for publication

## list
list
Outline
first review
second review
attribute validation
complete
Security | Security objects, RBAC
Billing | Dat items for billing
Network | Data items for electricity network measurements
Meter | Data items for meter management and communications management
remote
service interface
customer interface
remote + service
critical
private
neither
both
yes
maybe?
no
certification
comms mgmt
customer
data readout
fw upload
maintenance
management
pre-established
public
readout_gw
security officer

## Cover
Oe-Annex Version 1
TECHNICAL REPORT Annex
Comprehensive Semantic Model
for Energy Management
AC Electricity Smart Meter
Generic Companion Profile
Extended Object Model
DRAFT WORK IN PROGRESS
Oesterreichs Energie

## Syntax
Syntax
Syntax of ‘’Attribute Type’’ and ‘’Default Value’’ columns of Object Model file
The { } construction denotes an iteration of 0..n elements
The ¦ construction denotes a variant
The [ ] construction denotes an optional element
The red elements are terminal symbols
Syntax for the ‘’Attribute Type’’ column
TypeSpecifier ::= StandardType ¦ PredefinedType
StandardType ::= SimpleType ¦ ArrayType ¦ StructType ¦ OctetStringType ¦ ChoiceType
PredefinedType ::= types defined by the application, for example ass_list_type, and that can be defined with standard types or other predefined types.
SimpleType ::= null ¦ boolean ¦ bit_string ¦ double_long ¦ double_long_unsigned ¦ bcd ¦ integer ¦ long ¦ unsigned ¦ long_unsigned ¦ long64 ¦ long64_unsigned ¦ enum ¦ float32 ¦ float64 ¦ date_time ¦ time ¦ date
ArrayType ::= array [SizeConstraint] [(TypeSpecifier)]
StructType ::= struct{TypeSpecifier {, TypeSpecifier }}
OctetStringType ::= octet_string [SizeConstraint]
ChoiceType ::= choice(TypeSpecifier {, TypeSpecifier})
SizeConstraint ::= [Boundary [..Boundary]]
Boundary ::= IntegerValue ¦ *
Syntax for the Default Value column
Value ::= IntegerValue ¦ RangeValue ¦ StructuredValue ¦ StringValue ¦ VariantValue¦ OBISValue ¦ *
IntegerValue ::= [-] ?sequence of digits? ¦ 0x ?Sequence of hex-digits?
RangeValue ::= [Boundary.. Boundary]
Boundary ::= IntegerValue ¦ *
StructuredValue ::= {Value {, Value} [,…]}
StringValue ::= “\?Sequence of characters? ¦ ?even sequence of hex-digits”
VariantValue ::= choice(Value {,Value})
OBISValue ::= OBISField - OBISField: OBISField. OBISField. OBISField. OBISField
OBISField ::= IntegerValue ¦ RangeValue ¦ *
Extensions which control the supported objects
O=always optional
M=always mandatory
M-x mandatory for extension x
The '-x' defines the condition which applies to M, i.e. mandatory in case the condition is true.
-D=Extension D
-M=Extension M
-L=Extension L
-G=mobile communication channel is used (e.g. GPRS, UMTS, LTE, etc.)
-E=Ethernet communication channel is used
-G3=G3 PLC communication channel is used
-I4=IPv4 protocol is used
-I6=IPv6 protocol is used
-C=CIP supported
NA=not applicable
Colour Codes
Group Assignment
Instance
Attribute
Method
Note that original DLMS text is in black and modified or new text for Oe is in blue.
0

## Object model
# | Object / Attribute Name | Attribute Type | IC |  | SN | OBIS code / Default Value | Access rights | Access rights [Get, Set, Action], optional if in '( )' | [10 empty] | Mains Connection | [5 empty] | Functional Group | Extensions | Extensions |  |  | Com Profile | [7 empty] | Use Cases | Use Cases | [24 empty] | Comments
No | Object / Attribute Name | Attribute Type | Class | Ver. | Column1 | OBIS code / Default Value | AR | Public (16) | Preestablished (102) | Management (1) | Readout (2) | Readout-GW (8) | Maintenance (6) | Certification (7) | FW upload (3) | Comms mgmt(4) | Security Officer(20) | CII Role (103) | 1ph | 3ph | 1 ph Oe | 3 ph OE | 3 ph CT OE | Group | E | D | L | M | CP | SER | G3-PLC | CELL | Wi-SUN | LPWAN | Column6 | ETH | UC | UC1 | UC2 | UC3 | UC4 | UC5 | UC6 | UC7 | UC8 | UC9 | UC10 | UC11 | UC12 | UC13 | UC14 | UC15 | UC16 | UC17 | UC18 | UC19 | UC20 | UC21 | UC-Oe-01 | UC Oe-02 | UC Oe-03 | dummy | Comments | Oe-Comments
Abstract objects - Association & Security
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17 |  |  | UC20
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get | [45 empty] | One logical device, Server SAP 1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [11 empty] | UC13 |  |  |  | UC17 |  | UC19 | UC20
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | -- | -- | Action | Action | Action | Action | Action | Action | Action | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Association LN - Management association [1] |  | 15 | 3 |  | 0-0:40.0.1.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280001FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | Get
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Management Association (1) |  | 64 | 1 |  | 0-0:43.0.1.255 | [12 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [11 empty] | UC13 | [6 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0001FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | -- | Get | -- | -- | -- | Get, Set | [46 empty] | authenticated encryption required in both directions on all AAs except public (none) and CII (encryption only)
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action | [45 empty] | Root certificate may not be updated using this role.
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[19 empty] | M | M | M | M | M | BASIC | [31 empty] | UC19 | UC20
[8 empty] | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
[8 empty] | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [31 empty] | UC19 | UC20
[8 empty] | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
[8 empty] | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
| Association LN - Public association [16] |  | 15 | 3 |  | 0-0:40.0.16.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280010FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
2 | object_list | object_list_type |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
9 | security_setup_reference | octet_string[6] |  |  | 0x40 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
10 | user_list | array |  |  | 0x48 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Association LN - Data readout [2] |  | 15 | 3 |  | 0-0:40.0.2.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280002FF" |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
2 | object_list | object_list_type |  |  | 0x08 | (To be determined based on relevant Ucs) |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
3 | associated_partners_id | associated_partners_type |  |  | 0x10 | (To be discussed with the securtiy and architecture group, but Client L_SAP = 2) |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
4 | application_context_name | application_context_name |  |  | 0x18 | context_name_structure according 4.4.4.2.4 of BB17 pt 2 |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 | (negotiated at AARQ/AARE exchange) |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 | See 4.4.4.2.6 of BB17 part 2. mechanisms permitted are: HLS-GMAC (5) HLS-SHA-256 (6) HLS-ECDSA (7) Note that each company makes its own decision on which to use |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 |  |  | -- | -- | -- |  | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0002FF" |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
10 | user_list | array |  |  | 0x48 | <empty> |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 | no rights |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 | no rights |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 | no rights |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 | no rights |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Data readout [2] |  | 64 | 1 |  | 0-0:43.0.2.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0002FF" |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | Get | -- | -- | -- | -- | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | Get | -- | -- | -- | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 | (determined by Client) |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 | (GUID for meter) |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | -- | -- | -- | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
| Security - Receive frame counter - unicast key - Data readout |  | 1 | 0 |  | 0-0:43.1.66.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0142FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
| Association LN - Readout-GW [8] |  | 15 | 3 |  | 0-0:40.0.8.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280008FF" |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0008FF" |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | Action | -- | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Readout-GW [8] |  | 64 | 1 |  | 0-0:43.0.8.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0008FF" |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | Get | -- | -- | -- | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | -- | Get | -- | -- | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | Get | -- | -- | -- | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
| Security - Receive frame counter - unicast key - Readout-GW |  | 1 | 0 |  | 0-0:43.1.72.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0148FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
| Association LN - maintenance [6] |  | 15 | 3 |  | 0-0:40.0.6.255 | [14 empty] | M | M | M | BASIC | [13 empty] | UC1 | [18 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280006FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - maintenance [6] |  | 64 | 1 |  | 0-0:43.0.6.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0006FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action | [45 empty] | Root certificate may not be updated using this role.
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
| Security - Receive frame counter - unicast key - maintenance |  | 1 | 0 |  | 0-0:43.1.70.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0146FF" |  | Get | -- | Get | -- | -- | Get | -- | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | Get | -- | -- | -- | Get
| Association LN - Certification [7] |  | 15 | 3 |  | 0-0:40.0.7.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280007FF" |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | -- | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | --
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | Action | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Certification [7] |  | 64 | 1 |  | 0-0:43.0.7.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0007FF" |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | -- | -- | Get | -- | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | -- | -- | -- | Get | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | Get | -- | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
| Security - Receive frame counter - unicast key - certification |  | 1 | 0 |  | 0-0:43.1.71.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0147FF" |  | Get | -- | Get | -- | -- | -- | Get | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | Get | -- | -- | Get
| Association LN - Firmware Upload [3] (pre-established or not at buyers definition) |  | 15 | 3 |  | 0-0:40.0.3.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280003FF" |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | -- | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | --
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | Action | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Firmware Upload [3] |  | 64 | 1 |  | 0-0:43.0.3.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0003FF" |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | -- | -- | -- | Get | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | -- | -- | -- | -- | Get | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | -- | Get | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
| Security - Receive frame counter - broadcast key - Firmware Upload |  | 1 | 0 |  | 0-0:43.1.3.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0103FF" |  | Get | -- | Get | -- | -- | -- | -- | Get | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | Get | -- | Get
| Security - Receive frame counter - unicast key - Firmware Upload |  | 1 | 0 |  | 0-0:43.1.67.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0143FF" |  | Get | -- | Get | -- | -- | -- | -- | Get | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | Get | -- | Get
| Association LN - Comms mgmt [4] |  | 15 | 3 |  | 0-0:40.0.4.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [6 empty] | UC20 | [6 empty] | This is decided to be included.
1 | logical_name | octet_string[6] |  |  |  | "0000280004FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | -- | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | --
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | Action | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Comms mgmt [4] |  | 64 | 1 |  | 0-0:43.0.4.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [6 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0004FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | -- | -- | -- | -- | Get | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | -- | -- | -- | -- | -- | Get | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | Get | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | Action
| Security - Receive frame counter - broadcast key - Comms mgmt |  | 1 | 0 |  | 0-0:43.1.4.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [25 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0104FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | Get | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | Get | Get
| Security - Receive frame counter - unicast key - Comms mgmt |  | 1 | 0 |  | 0-0:43.1.68.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [25 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0144FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | Get | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | Get | Get
| Association LN - pre-established [102] |  | 15 | 3 |  | 0-0:40.0.102.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280066FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | -- | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | -- | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - pre-established [102] |  | 64 | 1 |  | 0-0:43.0.102.255 | [14 empty] | M | M | M | BASIC | [13 empty] | UC1 | [18 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0066FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | Action | -- | -- |  |  | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | Action | -- | -- |  |  | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | Action | -- | -- |  | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
| Security - Receive frame counter - broadcast key - pre-established |  | 1 | 0 |  | 0-0:43.1.102.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0166FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
| Security - Receive frame counter - unicast key - pre-established |  | 1 | 0 |  | 0-0:43.1.166.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B01A6FF" |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | -- | -- | -- | -- | -- | -- | Get
| Association LN - Security-officer [20] TBC |  | 15 | 3 |  | 0-0:40.0.20.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280014FF" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - Security-officer [20] |  | 64 | 1 |  | 0-0:43.0.20.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0014FF" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
2 | security_policy | enum |  |  | 0x08 | 108 - authenticated encrypted request, authenticated encrypted response |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get, Set
3 | security_suite | enum |  |  | 0x10 | 2 // applies to all Security Setup objects |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
4 | client_system_title | octet_string[8] |  |  | 0x18 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
5 | server_system_title | octet_string[8] |  |  | 0x20 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get
6 | certificates | array(struct(enum,enum,octet_string,octet_string,octet_string,octet_string)) |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Get | [45 empty] | Note that this is the only certificate set that manages the Root Certificate for the PKI.
1 | security_activate | enum |  |  | 0x30 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
2 | key_transfer | key_data |  |  | 0x38 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
3 | key_agreement | key_data |  |  | 0x40 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
4 | generate_key_pair | enum |  |  | 0x48 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
5 | generate_certificate_request | enum |  |  | 0x50 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
6 | import_certificate | octet_string |  |  | 0x58 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
7 | export_certificate | certificate_identification |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
8 | remove_certificate | certificate_identification |  |  | 0x68 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | Action
| Security - Receive frame counter - unicast key - Security-officer |  | 1 | 0 |  | 0-0:43.1.84.255 | [14 empty] | M | M | M | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00002B0154FF" |  | Get | -- | -- | -- | -- | -- | -- | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | -- | -- | -- | -- | -- | -- | -- | Get
| Association LN - CII |  | 15 | 3 |  | 0-0:40.0.103.255 | [14 empty] | M | M | M | BASIC | [24 empty] | UC12 | [7 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000280067FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
2 | object_list | object_list_type |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
3 | associated_partners_id | associated_partners_type |  |  | 0x10 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
4 | application_context_name | application_context_name |  |  | 0x18 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
5 | xDLMS_context_info | xDLMS_context_type |  |  | 0x20 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
6 | authentication_mechanism_name | mechanism_name_structure |  |  | 0x28 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | -- | [45 empty] | Optionally Set can be used to restrict the next association to a specific mechanism_name e.g. to mechnaism_name(5) after commisioning.
7 | secret | octet_string |  |  | 0x30 | "3132333435363738" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [45 empty] | In case of using LLS one can use attr 7 of Current Assoc. to change the LLS PW For HLS using GMAC secret is handled via Security setup
8 | association_status | enum |  |  | 0x38 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
9 | security_setup_reference | octet_string[6] |  |  | 0x40 | "00002B0000FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
10 | user_list | array |  |  | 0x48 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
11 | current_user | struct(unsigned,visible_string) |  |  | 0x50 |  |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
1 | reply_to_HLS_authentication | octet_string |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | change_HLS_secret | octet_string |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | -- | [45 empty] | For changing the HLS secret in case of using MD5 or SHA-1
3 | add_object |  |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | remove_object |  |  |  | 0x78 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | add_user |  |  |  | 0x80 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | remove_user |  |  |  | 0x88 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security setup - CII - (duplicate has been struck through) |  | 64 | 1 |  | 0-0:43.0.103.255 | [12 empty] | M | M | M | M | M | CII | [24 empty] | UC12 | [7 empty] | UC20
[8 empty] | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | Get, Set | [46 empty] | technically, request on this AA is impossible, but set to authenticated encrypted to prevent accidents.
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | Get, Set | [45 empty] | 0 = AES-GCM-128/AES-128
[8 empty] | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
[8 empty] | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
[8 empty] | -- | -- | Get | -- | -- | Get | -- | -- | -- | Get
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | Action
Abstract objects - ID's & Control information
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17 | [6 empty] | UC Oe-03
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[8 empty] | Get | -- | Get | Get | Get | Get | Get | Get | Get | Get
[19 empty] | M | M | O | O | O | BASIC | [14 empty] | UC2 | [24 empty] | not used
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [26 empty] | UC14
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | Action | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [26 empty] | UC14
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get, Set | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get, Set | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [26 empty] | UC14
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | -- | [46 empty] | maybe remove local port scripts if local port protection IC confirmed.
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
Abstract objects - Time related issues
[19 empty] | M | M | M | M | M | BASIC | [14 empty] | UC2 |  | UC4 | UC5 | UC6 | UC7 | UC8 |  |  | UC11 | UC12 | UC13
[8 empty] | -- | -- | Get | Get | Get | Get | Get | Get | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get, Set | Get, Set | Get, Set | Get | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | Get | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | Get | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | Get | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | Get | Get | --
[19 empty] | O | O |  |  |  | BASIC | [30 empty] | UC18
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | O | O |  |  |  | BASIC | [30 empty] | UC18
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [19 empty] | UC7
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | O | O | O | BASIC | [19 empty] | UC7
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Set | Get | Get | Set | -- | -- | -- | --
[8 empty] | -- | -- | Set | Get | Get | Set | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [14 empty] | UC2
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action |  | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [14 empty] | UC2
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [14 empty] | UC2
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[19 empty] | M | M | o | o | o | BASIC | [14 empty] | UC2
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [14 empty] | UC2
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Abstract objects - Billing period reset
[19 empty] | M | M | M | M | M | BASIC | [14 empty] | UC2 |  | UC4
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | Action | -- | -- | -- | [46 empty] | service interface needed, and also from HES, as welll as schedule.
[19 empty] | M | M | M | M | M | BASIC | [14 empty] | UC2 |  | UC4
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [14 empty] | UC2 |  | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | [6 empty] | BASIC
Abstract objects - Disconnector, Load mgmt, Supervision
[19 empty] | M | M | O | O |  | DISCO |  | D | [16 empty] | UC6 | [14 empty] | UC21
[8 empty] | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, (Set) | -- | -- | Get, (Set) | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | --
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6 | [14 empty] | UC21
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | Get | -- | -- | --
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6 | [14 empty] | UC21
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | LOAD |  |  | L | [18 empty] | UC9
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | LOAD |  |  | L | [18 empty] | UC9 | [11 empty] | UC21
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | LOAD |  |  | L | [18 empty] | UC9
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | LOAD |  |  | L | [18 empty] | UC9
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, (Set) | Get | Get | Get, (Set) | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | O | O | O | LOAD |  |  | L | [18 empty] | UC9
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, (Set) | Get | Get | Get, (Set) | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | O | O | M | M | M | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15 | [5 empty] | UC21 | [5 empty] | note - generates event only on CT meter
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, set | Get | -- | -- | -- | [46 empty] | The script should be empty as default.
[19 empty] | M | M | M | M |  | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15 | [5 empty] | UC21
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | NA | M | M | M |  | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | NA | M | M | M |  | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
Abstract objects - Errors & Alarms, Event logs
[19 empty] | M | M | M | M | M | BASIC | [23 empty] | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [19 empty] | UC7 |  |  |  | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [19 empty] | UC7 |  |  |  | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | PUSH | [19 empty] | UC7 |  |  |  | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | PUSH | [19 empty] | UC7 |  |  |  | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16 | UC17
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16 | UC17
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | PUSH | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16 | UC17
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | PUSH | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [14 empty] | UC2 |  |  |  |  | UC7 | UC8 |  | UC10 | UC11 |  |  | UC14 |  | UC16 |  |  | UC19 | UC20
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [14 empty] | UC2 |  |  |  |  | UC7 | UC8 |  | UC10 | UC11 |  |  | UC14 |  | UC16 |  |  | UC19 | UC20
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [23 empty] | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[19 empty] | M | M | M | M | M | BASIC | [23 empty] | UC11 |  |  |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get, | Get | -- | Get, | Get, | -- | -- | Get,
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get | [46 empty] | Note the use of sort method 2, to ensure that oldest values are retained.
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [25 empty] | UC13 | [5 empty] | UC19 | UC20
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[19 empty] | M | M | M | M | M | BASIC | [25 empty] | UC13 | [5 empty] | UC19 | UC20
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, | Get | -- | Get, | Get, | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[19 empty] | M | M | O | O | O | BASIC | [25 empty] | UC13 |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | Get
[19 empty] | M | M | 0 | 0 | 0 | BASIC | [25 empty] | UC13 |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | Get
[19 empty] | M | M | 0 | 0 | 0 | BASIC | [25 empty] | UC13 |  |  | UC16
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | Get
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [25 empty] | UC13 | [5 empty] | UC19 | UC20
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[19 empty] | M | M | M | M | M | BASIC | [25 empty] | UC13 | [5 empty] | UC19 | UC20
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get,Set | -- | -- | Get,Set | Get | -- | Get,Set | Get,Set
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | Get, Set | Get, Set
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | Get
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
Abstract objects - User Interface
[19 empty] | M | M | M | M | M | CII | [24 empty] | UC12 | [5 empty] | UC18
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | CII | [24 empty] | UC12 | [5 empty] | UC18
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | CII | [24 empty] | UC12
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [46 empty] | Oe - default every second.
[19 empty] | M | M | M | M | M | CII | [24 empty] | UC12
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | -- | Action
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M |  |  |  | CII | [24 empty] | UC12 | [7 empty] | UC20
[8 empty] | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Get | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | CII | [24 empty] | UC12
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | CII | [24 empty] | UC12
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Set | Get | Get | Set | Get | -- | -- | --
[8 empty] | -- | -- | Set | Get | Get | Set | Get | -- | -- | --
[8 empty] | -- | -- | Set | Get | Get | Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [30 empty] | UC18
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [30 empty] | UC18 |  |  |  |  | UC Oe-02
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get, Set | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Abstract objects - Firmware Upgrade
[19 empty] | M | M | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | -- | Get | -- | Get | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | Get, Set | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | -- | Get | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | -- | Get | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | Get | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | -- | Get | -- | -- | [46 empty] | mage
[8 empty] | -- | -- | Get | Get | -- | Get | -- | Get | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | Action | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | -- | Get | -- | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | -- | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | -- | Get | -- | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | O | O | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | O | O | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | O | O | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | O | O | M | M | M | BASIC | [22 empty] | UC10 | [13 empty] | UC Oe-03
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
Electricity related objects - Totals
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Electricity related objects - Rated registers
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Electricity related objects - Demand
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [15 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Electricity related objects - Profiles
[19 empty] | M | M | M | M | M | BASIC | [16 empty] | UC4 |  |  | UC7 | UC8 | [5 empty] | UC14
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [16 empty] | UC4 | UC5 | [8 empty] | UC14
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [16 empty] | UC4 |  |  | UC7 | [6 empty] | UC14
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [16 empty] | UC4 | UC5 | [8 empty] | UC14
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Electricity related objects - PQ, monitored values
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8 | [7 empty] | UC16
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8 | [7 empty] | UC16
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[11 empty] | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [46 empty] | Up to 20 attributes need to be captured in a record.
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | DISCO |  | D | [18 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | DISCO |  | D | [18 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | NA | M |  | M | M | DISCO |  | D | [18 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | O | O | O | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | DISCO |  | D | [18 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | DISCO |  | D | [18 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | D | D | D | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O | M | M | M | BASIC | [20 empty] | UC8
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Local communication - M-Bus
[19 empty] | M | M |  |  |  | MULT |  |  |  | M
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1 | [5 empty] | UC7
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1 | [5 empty] | UC7
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1 | [5 empty] | UC7
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1 | [5 empty] | UC7
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [11 empty] | UC3 | UC4 | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [9 empty] | UC1
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [13 empty] | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [13 empty] | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [13 empty] | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [13 empty] | UC5
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT |  |  |  | M | [13 empty] | UC5 | [8 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT |  |  |  | M | [13 empty] | UC5 | [8 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT |  |  |  | M | [13 empty] | UC5 | [8 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT |  |  |  | M | [13 empty] | UC5 | [8 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | M |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | O | O |  |  |  | MULT |  |  |  | M | [14 empty] | UC6
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT |  |  |  | M
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | O | O | O | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT |  |  |  | M | [21 empty] | UC13
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M |  |  |  | MULT | [19 empty] | UC7 | [8 empty] | UC16
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT | [19 empty] | UC7 | [6 empty] | UC14 |  | UC16
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT | [26 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT | [26 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | MULT | [26 empty] | UC14
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Local communication - IEC/HDLC Optical port
[19 empty] | M | M | M | M | M | COM | [5 empty] | SER | [19 empty] | UC14 | [5 empty] | UC19
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
[8 empty] | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
[8 empty] | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
[19 empty] | M | M | M | M | M | COM | [5 empty] | SER | [19 empty] | UC14 | [5 empty] | UC19
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
Abstract objects - TCP/IP profile setup
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | -- | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, set | -- | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[19 empty] | M | M | M | M | M | COM | [7 empty] | CELL |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | -- | Get |  | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC |  |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[19 empty] | M | M | M | M | M | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | -- | -- | -- | --
Abstract objects - Push setup
[19 empty] | M | M | M | M | M | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | Action | Action | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | -- | -- | -- | --
[8 empty] | -- | -- | Action | Action | Action | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11 | [15 empty] | Applied to EoBP push
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | Action | Action | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [13 empty] | UC1 |  |  |  | UC5 |  |  | UC8 |  |  | UC11 | [5 empty] | UC17
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [13 empty] | UC1 | [15 empty] | UC17 |  |  |  |  | UC-Oe-01 |  | UC Oe-03
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[19 empty] | M | M | M | M | M | PUSH | [13 empty] | UC1 | [15 empty] | UC17
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | -- | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[19 empty] | O | O | O | O | O | PUSH | [20 empty] | UC8 | [18 empty] | Note only meaningful on P2P
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [13 empty] | UC1 |  |  |  | UC5 |  |  | UC8 |  |  | UC11 | [5 empty] | UC17
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11 | [5 empty] | UC17
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11 | [5 empty] | UC17
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11 | [5 empty] | UC17
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
Remote communication - Abstract Objects for Network Mgmt
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | CELL |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
[19 empty] | M | M | O | O | O | COM | [6 empty] | G3-PLC |  |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
Remote communication - GSM/GPRS Setup Objects
[19 empty] | M | M | M | M | M | COM | [7 empty] | CELL | [17 empty] | UC13? | [8 empty] | UC-Oe-01 |  |  |  |  | Default values need to be part of DSO specific config-file; Further a second config Object for a secondary SIM (parallel route for QS) is needed by at least one DSO
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | COM | [7 empty] | CELL | [17 empty] | UC13? | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | COM | [7 empty] | CELL | [17 empty] | UC13? | [6 empty] | UC20 |  | UC-Oe-01 |  |  |  |  | In our understanding only relevant for 2G networks. Which are not in focus for next Gen Smart Meters. Since Object ist Mandatory we should keep it as it is.
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[8 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
[19 empty] | M | M | M | M | M | COM | [7 empty] | CELL | [17 empty] | UC13?
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
Remote communication - G3-PLC Setup Objects
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13? | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Action | -- | Action | Action | -- | -- | Action | --
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13? | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Set | Get | Get | Set | -- | -- | Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Action | -- | Action | Action | -- | -- | Action | --
[8 empty] | -- | -- | Action | -- | Action | Action | -- | -- | Action | --
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13? | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13?
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Action | -- | Action | Action | -- | -- | Action | --
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13? | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Action | -- | Action | Action | Action | -- | Action | --
[19 empty] | M | M | M | M | M | COM | [6 empty] | G3-PLC | [18 empty] | UC13? | [8 empty] | UC-Oe-01
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
[8 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
Abstract objects - Prepayment
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY |  | D | [16 empty] | UC6 | [14 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[19 empty] | M | M | D | D | D | PAY | [33 empty] | UC21
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
[8 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Austria-specific Objects (other than Role Control objects)
| Communication port protection |  | 124 | 0 |  | 0-0:44.2.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [26 empty] | UC14
1 | logical_name | octet_string[6] |  |  |  | "00002C0200FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | protection_mode | enum |  |  |  | 2 //unlocked |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
3 | allowed_failed_attempts | long_unsigned |  |  |  | 5 |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
4 | initial_lockout_time | double-long-unsigned |  |  |  | 60 //(seconds) |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
5 | steepness_factor | unsigned |  |  |  | 2 //See Blue Book for implication |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
6 | max_lockout_time | double-long-unsigned |  |  |  | 86400 //(seconds = 24 hours) |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
7 | port_reference | octet-string(6) |  |  |  | "" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
8 | protection_status | enum | [5 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
9 | failed_attempts | double-long-unsigned | [5 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
10 | cumulative_failed_attempts | double-long-unsigned | [5 empty] | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
1 | reset |  |  |  |  | 0 |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
| Threshold for anti-replay |  | 3 | 0 |  | 0-0:94.43.151.255 | [14 empty] | Yes | Yes | Yes | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00005E2B97FF" |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 | 4 |  | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {0,255} |  | -- | -- | Get | -- | -- | Get | -- | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Consumer - State of input/output control signals |  | 1 | 0 |  | 0-0:96.3.3.255 | [14 empty] | Yes | Yes | Yes | CII | [24 empty] | UC12 | [5 empty] | UC18 | [7 empty] | Consumer code showing status elements shown on meter's display & remote
1 | logical_name | octet_string[6] |  |  |  | "0000600303FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | bitstring(8) or ??? |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Status to be shown on numeric display.
| V.44 Control |  | 1 | 0 |  | 0-0:94.43.4.255 | [14 empty] | Yes | Yes | Yes | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00005E2B04FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | value | Boolean |  |  | 0x08 | TRUE = on, FALSE = off |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | -- | [46 empty] | Note that there will be a bit set in the APDU header to indicate whether V.44 is applied or not.
| V.44 Threshold |  | 1 | 0 |  | 0-0:94.43.5.255 | [14 empty] | Yes | Yes | Yes | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00005E2B05FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 | 200 bytes |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
| Metrological Error Register |  | 1 | 0 |  | 0-0:97.97.1.255 | [14 empty] | Yes | Yes | Yes | BASIC | [23 empty] | UC11 |  |  |  |  | UC16 | [10 empty] | Any error in this register is considered as legally relevant and causes the cancellation of its metrological certification. The bit-allocation in this Fatal Error Register is manufacturer specific. Resetting is not permitted ACTION to ensure that this is displayed on screen, as element like triange with !
1 | logical_name | octet_string[6] |  |  |  | "0000616101FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
2 | value | bit-string[8] |  |  |  | To be declared by the manufacturer |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
| Profile status - Load profile with period 3 |  | 1 | 0 |  | 0-0:96.10.3.255 | [14 empty] | Yes | Yes | Yes | BASIC | [16 empty] | UC4 |  |  | UC7 | UC8 | [5 empty] | UC14
1 | logical_name | octet_string[6] |  |  |  | "0000600A03FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | bitmask :: {PDN,reserved,CAD,reserved,DST,DNV,CIV,ERR}
| Load profile with period 3 |  | 7 | 1 |  | 1-0:99.1.4.255 | [14 empty] | Yes | Yes | Yes | BASIC | [16 empty] | UC4 | UC5 | [8 empty] | UC14
1 | logical_name | octet_string[6] |  |  |  | "0100630104FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | buffer | array |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | selective access per range and entry
3 | capture_objects | array[2..*](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, //Clock {1,0-0:96.10.1.255,2,0}, //Status {3,1-0:{1..8}.8.0.255,2,0}} /Registers x 8 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | clock;AMR profile status; +A;−A
4 | capture_period | double_long_unsigned |  |  | 0x18 | 900 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | 15 minutes
5 | sort_method | enum |  |  | 0x20 | [1] |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | unsorted (FIFO) or sorted (smallest)
6 | sort_object | capture_object_definition |  |  | 0x28 | choice({*,*-*:*.*.*.*,*,*}, {8,0-0:1.0.0.255,2,0}) |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | unsorted or sorted by clock depending on choice in attr. sort_method i.e. if sort_method=sorted then sort_object=0-0:1.0.0.255
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
8 | profile_entries | double_long_unsigned |  |  | 0x38 | [5760..*] For CT meters 43200 is permitted. |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | ≥10 days, optional set to restrict maximum capacity according to national laws
1 | reset |  |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
| Push setup - Interval_4 |  | 40 | 2 |  | 0-8:25.9.0.255 | [14 empty] | Yes | Yes | Yes | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11
1 | logical_name | octet_string[6] |  |  |  | "0008190900FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | push_object_list | array[0..*](push_object_definition) |  |  | 0x08 | {...} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | List of attributes to be pushed and associated parameters. The buffer is evaluated just before being tried to be sent for the first time or retried.
3 | send_destination_and_method | send_destination_and_method_type |  |  | 0x10 | {[0..8],*,0} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Destination address where the data specified by the push_object_list has to be sent, as well as the sending method
4 | communication_window | array[0..*](window_element) |  |  | 0x18 | {...} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Time points when the communication window(s) for the push become(s) active
5 | randomisation_start_interval | long_unsigned |  |  | 0x20 | 0 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Randomization time in seconds, 0 = no randomization at start of the first window defined in communication_window
6 | number_of_retries | unsigned |  |  | 0x28 | 0 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Max number of retransmissions of unsuccessful push
7 | repetition_delay | repetition_delay |  |  | 0x30 | {0,200,0} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Repetition delay min, exponent (x100), max
8 | port_reference | octet_string[0..6] |  |  | 0x38 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Logical name of a communication port setup object
9 | push_client_SAP | integer |  |  | 0x40 | 102 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Client SAP where the push is directed to in the supporting layer of the DataNotification service
10 | push_protection_parameters | array[0..2](protection_parameters_element) |  |  | 0x48 | {...} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Protection parameters to be applied to the DataNotification APDU, in the order they are applied if there are several elements.
11 | push_operation_method | enum |  |  | 0x50 | 0 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Defines if the DataNotification.request service primitive is invoked with Service_Class == Unconfirmed or Confirmed and how the push retry operates
12 | confirmation_parameters | confirmation_parameters |  |  | 0x58 | {"FFFFFFFFFFFFFFFFFF8000FF", 0} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Selection of entries defined by data_index to avoid pushing data from too far in the past
13 | last_confirmation_date | date_time |  |  | 0x60 | "FFFFFFFFFFFFFFFFFF8000FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | Date and time when the AL most recently invoked the DataNotification.confirm service primitive with Result == CONFIRMED
1 | push | integer |  |  | 0x68 | 0 |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | -- | [45 empty] | Activates the push process
2 | reset | integer |  |  | 0x70 | 0 |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | -- | [45 empty] | Resets the push process to initial state. Currently scheduled tries/retries are cancelled until the next trigger.
| Push action scheduler - Interval_4 |  | 22 | 0 |  | 0-4:15.0.4.255 | [14 empty] | Yes | Yes | Yes | PUSH | [17 empty] | UC5 |  |  | UC8 |  |  | UC11
1 | logical_name | octet_string[6] |  |  |  | "00040F0004FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | executed_script | script22 |  |  | 0x08 | {0-0:10.0.108.255,9} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
3 | type | enum |  |  | 0x10 | 5 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
4 | execution_time | array[0..*](execution_time_date) |  |  | 0x18 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
| LED 1 mode of operation |  | 1 | 0 |  | 0-0:96.10.3.255 | [14 empty] | Yes | Yes | Yes | BASIC | [16 empty] | UC4 |  |  | UC7 | UC8 | [14 empty] | UC Oe-02 |  |  |  | This enumeration determines the mode of operation of the LED 1.
1 | logical_name | octet_string[6] |  |  |  | "0000600A03FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | enum |  |  | 0x08 | 1 |  | -- | -- | Get, Set | Get | Get | Get,Set | Get, Set | -- | -- | -- | [45 empty] | Enum: 1 = Active Energy 2 = Reactive 3 = load profile 1 period start indication
| LED 1 (metrological) constant (active) |  | 3 | 0 |  | 1-0:0.3.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [35 empty] | UC Oe-02 |  |  |  | Note that this and/or the reactive value will be changed for calibration purposes, but the selection is determined by the Enumeration object.
1 | logical_name | octet_string[6] |  |  |  | "0100000300FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 | 1 |  | -- | -- | Get | -- | -- | Get, Set | Get, Set | -- | -- | -- | [46 empty] | If the value = 0, then the LED 1 follows the value determined by the reactive LED object.
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {0,30} // CT uses different value, often {-2,30} |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| LED 1 (metrological) constant (reactive) |  | 3 | 0 |  | 1-0:0.3.1.255 | [14 empty] | Yes | Yes | Yes | BASIC | [35 empty] | UC Oe-02 |  |  |  | Note that this and/or the active value will be changed for calibration purposes, but the selection is determined by the Enumeration object.
1 | logical_name | octet_string[6] |  |  |  | "0100000301FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 | 0 |  | -- | -- | Get | -- | -- | Get, Set | Get, Set | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {0,29} // CT uses different value, often {-2,29} |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| LED 1 pulse duration |  | 3 | 0 |  | 1-0:0.9.8.255 | [14 empty] | Yes | Yes | Yes | BASIC
1 | logical_name | octet_string[6] |  |  |  | "0100000908FF" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 | 50 |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,7} // milliseconds |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| LED 2 constant (reactive) |  | 3 | 0 |  | 1-1:0.3.1.255 | [14 empty] | O | O | O | BASIC | [35 empty] | UC Oe-02
1 | logical_name | octet_string[6] |  |  |  | "0101000301FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get, Set | Get, Set | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {0,29} // CT uses different value, often {-2,29} |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| LED 2 pulse duration |  | 3 | 0 |  | 1-1:0.9.8.255 | [14 empty] | O | O | O | BASIC
1 | logical_name | octet_string[6] |  |  |  | "0101000908FF" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 | 50 |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,7} // milliseconds |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Limiter (import 2) |  | 71 | 0 |  | 0-0:17.0.1.255 | [14 empty] | Yes | Yes | Yes | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15 | [5 empty] | UC21
1 | logical_name | octet_string[6] |  |  |  | "0000110001FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | monitored_value | value_definition |  |  | 0x08 | CHOICE { {3, 1-0:1.7.0.255,2}, {5, 1-0.1.4.0.255,2}, {3, 1-0:2.7.0.255,2}, {5, 1-0.2.4.0.255,2}} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | instantaneous current or sliding demand
3 | threshold_active | threshold |  |  | 0x10 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
4 | threshold_normal | threshold |  |  | 0x18 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Note. This attribute is used to configure the threshold
5 | threshold_emergency | threshold |  |  | 0x20 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
6 | min_over_threshold_duration | double_long_unsigned |  |  | 0x28 | 900 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
7 | min_under_threshold_duration | double_long_unsigned |  |  | 0x30 | 5 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
8 | emergency_profile | emergency_profile_type |  |  | 0x38 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
9 | emergency_profile_group_id_list | array |  |  | 0x40 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
10 | emergency_profile_active | boolean |  |  | 0x48 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
11 | actions | action_set |  |  | 0x50 | choice( { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,2} }, { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,0} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,2} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,0} }, { {0-0:10.0.103.255,5} , {0-0:10.0.103.255,6} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,0} }, ) |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [46 empty] | The script should be empty as default.
| Limiter (export 1) |  | 71 | 0 |  | 0-0:17.0.2.255 | [14 empty] | Yes | Yes | Yes | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15 | [5 empty] | UC21
1 | logical_name | octet_string[6] |  |  |  | "0000110002FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | monitored_value | value_definition |  |  | 0x08 | CHOICE { {3, 1-0:1.7.0.255,2}, {5, 1-0.1.4.0.255,2}, {3, 1-0:2.7.0.255,2}, {5, 1-0.2.4.0.255,2}} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | instantaneous current or sliding demand
3 | threshold_active | threshold |  |  | 0x10 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
4 | threshold_normal | threshold |  |  | 0x18 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Note. This attribute is used to configure the threshold
5 | threshold_emergency | threshold |  |  | 0x20 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
6 | min_over_threshold_duration | double_long_unsigned |  |  | 0x28 | 900 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
7 | min_under_threshold_duration | double_long_unsigned |  |  | 0x30 | 5 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
8 | emergency_profile | emergency_profile_type |  |  | 0x38 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
9 | emergency_profile_group_id_list | array |  |  | 0x40 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
10 | emergency_profile_active | boolean |  |  | 0x48 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
11 | actions | action_set |  |  | 0x50 | choice( { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,2} }, { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,0} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,2} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,0} }, { {0-0:10.0.103.255,5} , {0-0:10.0.103.255,6} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,0} }, ) |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [46 empty] | The script should be empty as default.
| Limiter (export 2) |  | 71 | 0 |  | 0-0:17.0.3.255 | [14 empty] | Yes | Yes | Yes | DISCO |  | D | [16 empty] | UC6 | [8 empty] | UC15 | [5 empty] | UC21
1 | logical_name | octet_string[6] |  |  |  | "0000110003FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | monitored_value | value_definition |  |  | 0x08 | CHOICE { {3, 1-0:1.7.0.255,2}, {5, 1-0.1.4.0.255,2}, {3, 1-0:2.7.0.255,2}, {5, 1-0.2.4.0.255,2}} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | instantaneous current or sliding demand
3 | threshold_active | threshold |  |  | 0x10 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
4 | threshold_normal | threshold |  |  | 0x18 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [45 empty] | Note. This attribute is used to configure the threshold
5 | threshold_emergency | threshold |  |  | 0x20 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
6 | min_over_threshold_duration | double_long_unsigned |  |  | 0x28 | 900 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
7 | min_under_threshold_duration | double_long_unsigned |  |  | 0x30 | 5 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
8 | emergency_profile | emergency_profile_type |  |  | 0x38 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
9 | emergency_profile_group_id_list | array |  |  | 0x40 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
10 | emergency_profile_active | boolean |  |  | 0x48 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
11 | actions | action_set |  |  | 0x50 | choice( { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,2} }, { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,0} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,2} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,0} }, { {0-0:10.0.103.255,5} , {0-0:10.0.103.255,6} }, { {0-0:10.0.103.255,1} , {0-0:10.0.103.255,0} }, ) |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | -- | [46 empty] | The script should be empty as default.
| Certification Log |  | 7 | 1 |  | 0-0:99.98.7.255 | [14 empty] | Yes | Yes | Yes | BASIC | [31 empty] | UC19 | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000636207FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | buffer | array |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | selective access per range
3 | capture_objects | array[8..*](capture_object_definition) |  |  | 0x10 | {{0-0:1.0.0.255,2}, {0-0:96.11.7.255,2)} Reconfiguration not permitted. Over-writing not permitted |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | choice because of extension M
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | asynchronously
5 | sort_method | enum |  |  | 0x20 | 2 |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [46 empty] | Note the use of sort method 2, to ensure that oldest values are retained.
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | unsorted
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
8 | profile_entries | double_long_unsigned |  |  | 0x38 | [300..*] |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
1 | reset | integer |  |  | 0x58 | NOT PERMITTED |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Event Object - Certification Log |  | 1 | 0 |  | 0-0:96.11.7.255 | [14 empty] | Yes | Yes | Yes | BASIC | [31 empty] | UC19 | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600B07FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | choice(enum, long_unsigned) |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Max Voltage L1 |  | 3 | 0 |  | 1-0:32.26.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100201A00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-1,35} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Max Voltage L2 |  | 3 | 0 |  | 1-0:52.26.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100341A00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-1,35} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Max Voltage L3 |  | 3 | 0 |  | 1-0:72.26.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100481A00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-1,35} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Min Voltage L1 |  | 3 | 0 |  | 1-0:32.23.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100201700FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-1,35} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Min Voltage L2 |  | 3 | 0 |  | 1-0:52.23.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100341700FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-1,35} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Min Voltage L3 |  | 3 | 0 |  | 1-0:72.23.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100481700FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-1,35} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Max current L1 |  | 3 | 0 |  | 1-0:31.26.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "01001F1A00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | Whole Current {-1,33}, CT {-2,33} 0r {-3,33} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Max current L2 |  | 3 | 0 |  | 1-0:51.26.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100331A00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | Whole Current {-1,33}, CT {-2,33} 0r {-3,33} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Max current L3 |  | 3 | 0 |  | 1-0:71.26.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100471A00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | Whole Current {-1,33}, CT {-2,33} 0r {-3,33} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Min Power Factor L1 |  | 3 | 0 |  | 1-0:33.23.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100211700FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Min Power Factor L2 |  | 3 | 0 |  | 1-0:53.23.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100351700FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Min Power Factor L3 |  | 3 | 0 |  | 1-0:73.23.0.255 | [15 empty] | Yes | Yes | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100491700FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | 10 minutes
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Connection Watchdog Timer |  | 1 | 0 |  | 0-0:94.43.7.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [13 empty] | A watchdog timer makes sure that the modem resets the connection after a defined period of no contact with the CS.
1 | logical_name | octet_string[6] |  |  |  | "00005E2B07FF" |  | -- | -- | Get | Get | -- | Get | -- | -- | Get | --
2 | value | long_unsigned |  |  |  | 6 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | Get, Set | --
| Periodical Self-Check Timer |  | 1 | 0 |  | 0-0:94.43.6.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [13 empty] | The time interval for initiating a self-check of the modem can be configured and managed
1 | logical_name | octet_string[6] |  |  |  | "00005E2B06FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  |  | 1440 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | Get, Set | --
| LTE Monitoring |  | 151 | 1 |  | 0-0:25.11.0.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000190B00FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | LTE_network_parameters | LTE_network_ parameters_type | [5 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | LTE_quality_of_service | LTE_QoS_type | [5 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| CHAP password |  | 1 | 0 |  | 0-0:94.43.20.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | needed by NOÖ
1 | logical_name | octet_string[6] |  |  |  | "00005E2B14FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string[64] | [5 empty] | -- | -- | Get, Set | -- | -- | Get, Set | -- | -- | -- | --
--
| Telecom IRAT Timer |  | 1 | 0 |  | 0-0:96.61.2.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Timer for when a switchover to next CELL tech should happen
1 | logical_name | octet_string[6] |  |  |  | "0000603D02FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  |  | 120(min) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [46 empty] | must not be lower than 1h (to prevent frequent "hopping"
| Telecom CAT-M switch threshold |  | 1 | 0 |  | 0-0:96.61.3.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when CAT-M should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "0000603D03FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | long |  |  |  | -115(dbm) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
| Telecom CATM-NBIOT switch threshold |  | 1 | 0 |  | 0-0:96.61.4.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "0000603D04FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | long |  |  |  | -125(dbm) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | --
| G3-PLC Key |  | 1 | 0 |  | 0-0:94.43.30.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1EFF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string | [5 empty] | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
| G3-PLC KEK |  | 1 | 0 |  | 0-0:94.43.31.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1FFF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string |  |  |  | -125(dbm) |  | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
| G3-PLC Key pending |  | 1 | 0 |  | 0-0:94.43.30.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1E00" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string | [5 empty] | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
| G3-PLC KEK pending |  | 1 | 0 |  | 0-0:94.43.31.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1F00" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string |  |  |  | -125(dbm) |  | -- | -- | Set | -- | -- | Set | -- | -- | -- | --
| G3-PLC Key Backup |  | 1 | 0 |  | 0-0:94.43.30.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1EFE" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string | [5 empty] | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| G3-PLC KEK backup |  | 1 | 0 |  | 0-0:94.43.31.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1FFE" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | octet_string |  |  |  | -125(dbm) |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| PLCG3TimeOut |  | 1 | 0 |  | 0-0:94.43.10.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0AFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  | 2160 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | This data defines the time, in minutes, after which a meter that has not been individually addressed (meaning the meter has not received any Path Discovery message, ICMP ping, nor unicast DLMS APDU) returns to the non associated state and loses its PAN coordinator. A value equal to 0 is equivalent to cancel the use of the related time-out-not-addressed counter. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 2160 (36h)
| PLCG3KeepAlive |  | 1 | 0 |  | 0-0:94.43.11.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0BFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure { keep_alive_enable keep_alive_start_time keep_alive_send_period } |  |  |  | { 0;300;10} |  | -- | -- | Get, Set | Get | Get, Set | Get, Set | Get | -- | Get, Set | -- | [46 empty] | keep_alive_enable This parameter indicates whether the keep alive mechanism is enabled or not. Data type: BOOLEAN Authorized value: 0: FALSE The keep alive mechanism is disabled 1: TRUE The keep alive mechanism is enabled Default value: 0 keep_alive_start_time This parameter indicates the time in minutes to wait before starting the periodic emission of ICMP Echo requests. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 300 keep_alive_send_period This parameter indicates the time in minutes between two successive keep alive ICMP Echo requests. Data type: UNSIGNED8 Authorized value: 1 to 255 Default value: 10
| AdpLBPAssociationSetup |  | 1 | 0 |  | 0-0:94.43.14.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | This object contains parameters for Bootstrapping procedure setup - couldn't be identified in GCP "G3-PLC MAC 6LoWPAN adaptation layer setup" please DOUBLE CHECK
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0EFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure { Association_max_retry: unsigned8 Association_rand_wait_time_step: unsigned8 Association_alt_PAN: boolean Join_LQI_threshold: unsigned8 Active_scan_duration: unsigned8 } |  |  |  | {8;15;1;52,15} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | Association_max_retry This attribute indicates the maximum number of association retries carried out for one PAN. Authorized value: 1 to 255 Association_rand_wait_time_step This attribute indicates the waiting window time step in minutes between two associations retries for the same PAN. Authorized value : 0 to 255 Association_alt_PAN This attribute indicates whether or not the device tries to join an alternate PAN after reaching Association_max_retry retries. Authorized value : 0 : FALSE 1 : TRUE Join_LQI_threshold This attribute specifies the LQI threshold value to be used for LBA and PAN selection. Authorized value : 0 to 255 Active_scan_duration This attribute specifies the duration in seconds of the active scan. It is recommended that this attribute is greater than mac_beacon_randomization_window_length. Authorized value : 0 to 255
| AdpRREPWait |  | 1 | 0 |  | 0-0:94.43.15.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | A meter shall wait adp_RREP_Wait seconds between two successive RREP generations - couldn't be found in GCP, please double check
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0FFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [46 empty] | Removed - included in adp_routing_configuration attribute of IC=92
2 | value | unsigned |  |  |  | 10 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | value adp_RREP_Wait time in seconds Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 10
| MacCoherentTransmission |  | 1 | 0 |  | 0-0:94.43.12.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Indicates the coherent modulation scheme to set in the tone map response - couldn't be found in GCP, please double check and add if not standard
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0CFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 0 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | value Data type: ENUMERATED Authorized values: 0 only differential modulation scheme shall be set in tone map response 1 only coherent modulations scheme shall be set in tone map response 2 Either coherent or differential scheme may be set in tone map response. Default value: 0
| macSNRdBUseDiff8PSK |  | 1 | 0 |  | 0-0:94.43.13.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0DFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure of Unsigned {MAC_SNRDBROBO_ID MAC_SNRDBDBPSK_ID MAC_SNRDBDQPSK_ID MAC_SNRDBD8PSK_ID} |  |  |  | 0 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | indicates the number of dB with respect to the macSNRdBD8PSK threshold to force the tone map algorithm to ask for differential scheme - part of mac coherent transmission | Unsigned maps to Unsigned8.
| InitiatorElectricalPhase |  | 1 | 0 |  | 0-0:96.62.0.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | couldn't be found - double Check an add if not already existing
1 | logical_name | octet_string[6] |  |  |  | "0000603E00FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 0 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | This attribute is written by the client system to indicate the phase number to which the client is connected. The local node (meter) must not modify the value of this parameter. Only the DLMS/COSEM client may modify this parameter. value Data type: ENUMERATED Authorized values: 0: Not defined 1: Phase 1 2: Phase 2 3: Phase 3 Default value : 0 (Not defined)
| DeltaElectricalPhase |  | 1 | 0 |  | 0-0:96.62.1.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | couldn't be found - double Check an add if not already existing
1 | logical_name | octet_string[6] |  |  |  | "0000603E01FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | enum | [5 empty] | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | This attribute indicates the phase difference between the client system's connecting phase and the meter's connecting phase. The meter uses the information available from the G3-PLC layer. Enumerated description: 0 = Not defined, 1 = The meter is connected to the same phase as the client system, 2 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to 60 degrees, 3 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to 120 degrees, 4 = The phase difference between the meterr's connecting phase and the client system's connecting phase is equal to 180 degrees, 5 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to -120 degrees, 6 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to -60 degrees. Data type: ENUMERATED Authorized values: 0: Not defined 1: 0 degree 2: 60 degrees 3: 120 degrees 4: 180 degrees 5: -120 degrees 6: -60 degrees
| Security -CII Send frame counter |  | 1 | 0 |  | 0-0:43.1.103.255 | [14 empty] | Yes | Yes | Yes | CII | [24 empty] | UC12 | [7 empty] | UC20 |  | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00002B0167FF" |  | Get | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 |  |  | Get | -- | Get | Get | Get | Get | Get | -- | -- | --
| P2P event codes log |  | 7 | 1 |  | 0-0:99.98.9.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 |  |  | UC16 | [5 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000636209FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | buffer | array |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | selective access per range
3 | capture_objects | array[8..*](capture_object_definition) |  |  | 0x10 | {{0-0:1.0.0.255,2}, {0-0:96.11.89.255,2}} |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | Get, Set | -- | [45 empty] | choice because of extension M
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | asynchronously
5 | sort_method | enum |  |  | 0x20 | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | unsorted (FIFO)
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | unsorted
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
8 | profile_entries | double_long_unsigned |  |  | 0x38 | [10..*] |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
1 | reset | integer |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
| Event Object - P2P Event Codes Log |  | 1 | 0 |  | 0-0:96.11.8.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 |  |  | UC16 | [5 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000600B08FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | LastReject information { Reject cause Reject mcc, Reject mnc, Reject timestamp, } |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
| Alarm Register 3 |  | 1 | 0 |  | 0-0:97.98.2.255 | [14 empty] | Yes | Yes | Yes | BASIC | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16
1 | logical_name | octet_string[6] |  |  |  | "0000616202FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | Get
| Alarm Filter 3 |  | 1 | 0 |  | 0-0:97.98.12.255 | [14 empty] | Yes | Yes | Yes | BASIC | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16
1 | logical_name | octet_string[6] |  |  |  | "000061620CFF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get | [45 empty] | This filter defines, if an event is handled as an alarm when it appears
| Alarm Descriptor 3 |  | 1 | 0 |  | 0-0:97.98.22.255 | [14 empty] | Yes | Yes | Yes | PUSH | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16
1 | logical_name | octet_string[6] |  |  |  | "0000616216FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
2 | value | double_long_unsigned |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get | [45 empty] | Updated on Alarm register change i.e. on 0->1 transition of any of the bits in Alarm register the corresponding bit in the Alarm descriptor is set
| Alarm Monitor 3 |  | 21 | 0 |  | 0-0:16.1.2.255 | [14 empty] | Yes | Yes | Yes | PUSH | [13 empty] | UC1 | [6 empty] | UC8 |  |  | UC11 |  |  |  |  | UC16
1 | logical_name | octet_string[6] |  |  |  | "0000100102FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
2 | thresholds | array[1](double_long_unsigned) |  |  | 0x08 | {0} |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get | [45 empty] | Monitored value is Alarm descriptor 1. Value 0 in threshold means if any of the bits in monitor value is newly triggered the action of the monitor will be set.
3 | monitored_value | value_definition |  |  | 0x10 | {1, 0-0:97.98.22.255, 2} |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | Get
4 | actions | array[1](action_set) |  |  | 0x18 | {{{0-0:10.0.108.255,4} , {0-0:10.0.108.255,0}}} |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | Get | [45 empty] | triggers push on alarm in case of occurence, no action is triggered in case the alarm descriptor is cleared
| TCP-UDP setup -Pending |  | 41 | 0 |  | 0-0:25.0.0.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "000019000000" |  | -- | -- | Get | Get | Get | Get | -- | -- | Get | --
2 | TCP-UDP_port | long_unsigned |  |  | 0x08 | choice(4059, 61616) |  | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
3 | IP_reference | octet_string[6] |  |  | 0x10 | Choice(0-0:25.1.0.255,0-0:25.7.0.255) |  | -- | -- | Get, Set | Get | Get | Get, set | -- | -- | Get | -- | [45 empty] | optional set to allow switching from IPv4 to IPv6
4 | MSS | long_unsigned |  |  | 0x18 | 1280 |  | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
5 | nb_of_sim_conn | unsigned |  |  | 0x20 | 1 |  | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
6 | inactivity_time_out | long_unsigned |  |  | 0x28 | 180 |  | -- | -- | Get, Set | Get | Get | Get, Set | -- | -- | Get, Set | --
| IPv4 setup - Pending |  | 42 | 0 |  | 0-0:25.1.0.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "000019010000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | DL_reference | octet_string[6] |  |  | 0x08 | Choice(0-0:25.3.0.255, 0-0:25.2.0.255) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
3 | IP_address | double_long_unsigned |  |  | 0x10 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
4 | multicast_IP_address | array[0..*] |  |  | 0x18 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
5 | IP_options | array[0..*] |  |  | 0x20 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
6 | subnet_mask | double_long_unsigned |  |  | 0x28 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
7 | gateway_IP_address | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
8 | use_DHCP_flag | boolean |  |  | 0x38 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
9 | primary_DNS_address | double_long_unsigned |  |  | 0x40 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
10 | secondary_DNS_address | double_long_unsigned |  |  | 0x48 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
1 | add_mc_IP_address | double_long_unsigned |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | delete_mc_IP_address | double_long_unsigned |  |  | 0x68 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
3 | get_nbof_mc_IP_addresses | unsigned |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| IPv6 setup - Pending |  | 48 | 0 |  | 0-0:25.7.0.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC |  |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "000019070000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | DL_reference | octet_string[6] |  |  | 0x08 | Choice(0-0:25.3.0.255, 0-0:25.2.0.255) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
3 | address_config_mode | enum |  |  | 0x10 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
4 | unicast_IPv6_addresses | array[0..*](IPv6_address) |  |  | 0x18 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
5 | multicast_IPv6_addresses | array[0..*](IPv6_address) |  |  | 0x20 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
6 | gateway_IPv6_address | array[0..*](IPv6_address) |  |  | 0x28 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
7 | primary_DNS_address | IPv6_address |  |  | 0x30 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
8 | secondary_DNS_address | IPv6_address |  |  | 0x38 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
9 | traffic_class | unsigned |  |  | 0x40 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
10 | neighbor_discovery_setup | array[0..*](neighbour_discovery_setup_element) |  |  | 0x48 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
1 | add_IPv6_address | IPv6_address_entry |  |  | 0x60 |  |  | -- | -- | Action | -- | -- | Action | Action | -- | Action | --
2 | remove_IPv6_address | IPv6_address_entry |  |  | 0x68 |  |  | -- | -- | Action | -- | -- | Action | Action | -- | Action | --
| PPP setup - Pending |  | 44 | 0 |  | 0-0:25.3.0.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "000019030000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | PHY_reference | octet_string[6] |  |  | 0x08 | 0-0:25.4.0.255 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
3 | LCP_options | array[1..8](LCP_options_element) |  |  | 0x10 | { {3, 4, 0xC023},... } |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | { LCP-option-type := Auth-Prot, LCP-Option-Length := 2, LCP-option-data := PAP}
4 | IPCP_options | array[1..5](IPCP_options_element) |  |  | 0x18 | { {2, 4, 0x0000},... } |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | { IPCP-option-type := IP-comp-prot, IPCP-option-Length := 2, IPCP-option-data := No-IP-Compresion-is-used}
5 | PPP_authentication | PPP_authentication_type |  |  | 0x20 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | { choice( NULL, { user-name, PAP-password} ) }
| Connection Watchdog Timer - pending |  | 1 | 0 |  | 0-0:94.43.7.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | A watchdog timer makes sure that the modem resets the connection after a defined period of no contact with the CS.
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0700" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  |  | 6 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| Periodical Self-Check Timer - pending |  | 1 | 0 |  | 0-0:94.43.6.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | The time interval for initiating a self-check of the modem can be configured and managed
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0600" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  |  | 1440 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| CHAP password - pending |  | 1 | 0 |  | 0-0:94.43.20.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | needed by NOÖ
1 | logical_name | octet_string[6] |  |  |  | "00005E2B1400" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | octet_string[64] | [5 empty] | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| Telecom CAT-M switch threshold - pending |  | 1 | 0 |  | 0-0:96.61.3.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when CAT-M should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "0000603D0300" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long |  |  |  | -115(dbm) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| Telecom CATM-NBIOT switch threshold - pending |  | 1 | 0 |  | 0-0:96.61.4.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "0000603D0400" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long |  |  |  | -125(dbm) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| PLCG3TimeOut -pending |  | 1 | 0 |  | 0-0:94.43.10.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0A00" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  | 2160 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [46 empty] | This data defines the time, in minutes, after which a meter that has not been individually addressed (meaning the meter has not received any Path Discovery message, ICMP ping, nor unicast DLMS APDU) returns to the non associated state and loses its PAN coordinator. A value equal to 0 is equivalent to cancel the use of the related time-out-not-addressed counter. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 2160 (36h)
| AdpLBPAssociationSetup - pending |  | 1 | 0 |  | 0-0:94.43.14.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | This object contains parameters for Bootstrapping procedure setup - couldn't be identified in GCP "G3-PLC MAC 6LoWPAN adaptation layer setup" please DOUBLE CHECK
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0E00" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | structure { Association_max_retry: unsigned8 Association_rand_wait_time_step: unsigned8 Association_alt_PAN: boolean Join_LQI_threshold: unsigned8 Active_scan_duration: unsigned8 } |  |  |  | {8;15;1;52,15} |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [46 empty] | Association_max_retry This attribute indicates the maximum number of association retries carried out for one PAN. Authorized value: 1 to 255 Association_rand_wait_time_step This attribute indicates the waiting window time step in minutes between two associations retries for the same PAN. Authorized value : 0 to 255 Association_alt_PAN This attribute indicates whether or not the device tries to join an alternate PAN after reaching Association_max_retry retries. Authorized value : 0 : FALSE 1 : TRUE Join_LQI_threshold This attribute specifies the LQI threshold value to be used for LBA and PAN selection. Authorized value : 0 to 255 Active_scan_duration This attribute specifies the duration in seconds of the active scan. It is recommended that this attribute is greater than mac_beacon_randomization_window_length. Authorized value : 0 to 255
| MacCoherentTransmission - pending |  | 1 | 0 |  | 0-0:94.43.12.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Indicates the coherent modulation scheme to set in the tone map response - couldn't be found in GCP, please double check and add if not standard
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0C00" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [46 empty] | value Data type: ENUMERATED Authorized values: 0 only differential modulation scheme shall be set in tone map response 1 only coherent modulations scheme shall be set in tone map response 2 Either coherent or differential scheme may be set in tone map response. Default value: 0
| macSNRdBUseDiff8PSK - pending |  | 1 | 0 |  | 0-0:94.43.13.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0D00" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | structure of Unsigned {MAC_SNRDBROBO_ID MAC_SNRDBDBPSK_ID MAC_SNRDBDQPSK_ID MAC_SNRDBD8PSK_ID} |  |  |  | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | indicates the number of dB with respect to the macSNRdBD8PSK threshold to force the tone map algorithm to ask for differential scheme - part of mac coherent transmission | Unsigned maps to Unsigned8.
| Module system configuration - pending |  | 1 | 0 |  | 0-0:94.43.8.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0800" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 6 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [46 empty] | (0) Automatic. Cat-M is preferred, (1) GSM, (4) NB-Iot only (5) Cat-M only (6) Automatic. NB-Iot is preferred
| Module server configuration - pending |  | 1 | 0 |  | 0-0:96.5.2.0 | [14 empty] | Yes | Yes | Yes | COM | [25 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "000060050200" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 1 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [13 empty] | G3-PLC | CELL |  |  |  | ETH | [27 empty] | enum: (0) TCP_Server, (1) UDP_Server(Default)
| TCP-UDP setup -Backup |  | 41 | 0 |  | 0-0:25.0.0.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000190000FE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | TCP-UDP_port | long_unsigned |  |  | 0x08 | choice(4059, 61616) |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
3 | IP_reference | octet_string[6] |  |  | 0x10 | Choice(0-0:25.1.0.255,0-0:25.7.0.255) |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | optional set to allow switching from IPv4 to IPv6
4 | MSS | long_unsigned |  |  | 0x18 | 1280 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
5 | nb_of_sim_conn | unsigned |  |  | 0x20 | 1 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
6 | inactivity_time_out | long_unsigned |  |  | 0x28 | 180 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
| IPv4 setup - backup |  | 42 | 0 |  | 0-0:25.1.0.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000190100FE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | DL_reference | octet_string[6] |  |  | 0x08 | Choice(0-0:25.3.0.255, 0-0:25.2.0.255) |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
3 | IP_address | double_long_unsigned |  |  | 0x10 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
4 | multicast_IP_address | array[0..*] |  |  | 0x18 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
5 | IP_options | array[0..*] |  |  | 0x20 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
6 | subnet_mask | double_long_unsigned |  |  | 0x28 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
7 | gateway_IP_address | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
8 | use_DHCP_flag | boolean |  |  | 0x38 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
9 | primary_DNS_address | double_long_unsigned |  |  | 0x40 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
10 | secondary_DNS_address | double_long_unsigned |  |  | 0x48 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
1 | add_mc_IP_address | double_long_unsigned |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | delete_mc_IP_address | double_long_unsigned |  |  | 0x68 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
3 | get_nbof_mc_IP_addresses | unsigned |  |  | 0x70 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| IPv6 setup - Backup |  | 48 | 0 |  | 0-0:25.7.0.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC |  |  |  |  | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000190700FE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | DL_reference | octet_string[6] |  |  | 0x08 | Choice(0-0:25.3.0.255, 0-0:25.2.0.255) |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
3 | address_config_mode | enum |  |  | 0x10 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
4 | unicast_IPv6_addresses | array[0..*](IPv6_address) |  |  | 0x18 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
5 | multicast_IPv6_addresses | array[0..*](IPv6_address) |  |  | 0x20 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
6 | gateway_IPv6_address | array[0..*](IPv6_address) |  |  | 0x28 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
7 | primary_DNS_address | IPv6_address |  |  | 0x30 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
8 | secondary_DNS_address | IPv6_address |  |  | 0x38 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
9 | traffic_class | unsigned |  |  | 0x40 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
10 | neighbor_discovery_setup | array[0..*](neighbour_discovery_setup_element) |  |  | 0x48 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
1 | add_IPv6_address | IPv6_address_entry |  |  | 0x60 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | remove_IPv6_address | IPv6_address_entry |  |  | 0x68 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| PPP setup - Backup |  | 44 | 0 |  | 0-0:25.3.0.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000190300FE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | PHY_reference | octet_string[6] |  |  | 0x08 | 0-0:25.4.0.255 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
3 | LCP_options | array[1..8](LCP_options_element) |  |  | 0x10 | { {3, 4, 0xC023},... } |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | { LCP-option-type := Auth-Prot, LCP-Option-Length := 2, LCP-option-data := PAP}
4 | IPCP_options | array[1..5](IPCP_options_element) |  |  | 0x18 | { {2, 4, 0x0000},... } |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | { IPCP-option-type := IP-comp-prot, IPCP-option-Length := 2, IPCP-option-data := No-IP-Compresion-is-used}
5 | PPP_authentication | PPP_authentication_type |  |  | 0x20 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | { choice( NULL, { user-name, PAP-password} ) }
| GPRS modem setup - pending |  | 45 | 0 |  | 0-0:25.4.0.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Default values need to be part of DSO specific config-file; Further a second config Object for a secondary SIM (parallel route for QS) is needed by at least one DSO
1 | logical_name | octet_string[6] |  |  |  | "000019040000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | APN | octet_string[0..64] |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | An APN with a size of 64 bytes at least is supported, i.e. [0.64] is mandatoty but can be longer
3 | PIN_code | long_unsigned |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | quality_of_service | quality_of_service_type |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Modem configuration - pending |  | 27 | 1 |  | 0-0:2.0.0.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "000002000000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | comm_speed | enum |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | initialization_string | array |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | modem_profile | array |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Auto answer - pending |  | 28 | 2 |  | 0-0:2.2.0.0 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [6 empty] | UC20 |  | UC-Oe-01 |  |  |  |  | In our understanding only relevant for 2G networks. Which are not in focus for next Gen Smart Meters. Since Object ist Mandatory we should keep it as it is.
1 | logical_name | octet_string[6] |  |  |  | "000002020000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | mode | enum |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | listening_window | array[0..*] |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | Array[0] equals always listening
4 | status | enum |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
5 | number_of_calls | unsigned |  |  | 0x20 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | number_of_rings | nr_rings_type |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | list_of_allowed_callers | array[0..*](list_of_allowed_callers_element) |  |  | 0x30 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | phone number is an ASCII coded octet-string of phone number length
| GPRS modem setup - backup |  | 45 | 0 |  | 0-0:25.4.0.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Default values need to be part of DSO specific config-file; Further a second config Object for a secondary SIM (parallel route for QS) is needed by at least one DSO
1 | logical_name | octet_string[6] |  |  |  | "0000190400FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | APN | octet_string[0..64] |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | An APN with a size of 64 bytes at least is supported, i.e. [0.64] is mandatoty but can be longer
3 | PIN_code | long_unsigned |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | quality_of_service | quality_of_service_type |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Modem configuration - backup |  | 27 | 1 |  | 0-0:2.0.0.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000020000FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | comm_speed | enum |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | initialization_string | array |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | modem_profile | array |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Auto answer - backup |  | 28 | 2 |  | 0-0:2.2.0.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [6 empty] | UC20 |  | UC-Oe-01 |  |  |  |  | In our understanding only relevant for 2G networks. Which are not in focus for next Gen Smart Meters. Since Object ist Mandatory we should keep it as it is.
1 | logical_name | octet_string[6] |  |  |  | "0000020200FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | mode | enum |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | listening_window | array[0..*] |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | Array[0] equals always listening
4 | status | enum |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
5 | number_of_calls | unsigned |  |  | 0x20 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | number_of_rings | nr_rings_type |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | list_of_allowed_callers | array[0..*](list_of_allowed_callers_element) |  |  | 0x30 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | phone number is an ASCII coded octet-string of phone number length
| Connection Watchdog Timer - backup |  | 1 | 0 |  | 0-0:94.43.7.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | A watchdog timer makes sure that the modem resets the connection after a defined period of no contact with the CS.
1 | logical_name | octet_string[6] |  |  |  | "00005E2B07FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  |  | 6 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Periodical Self-Check Timer - backup |  | 1 | 0 |  | 0-0:94.43.6.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | The time interval for initiating a self-check of the modem can be configured and managed
1 | logical_name | octet_string[6] |  |  |  | "00005E2B06FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  |  | 1440 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| CHAP password - backup |  | 1 | 0 |  | 0-0:94.43.20.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | needed by NOÖ
1 | logical_name | octet_string[6] |  |  |  | "00005E2B14FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | octet_string[64] | [5 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Telecom CAT-M switch threshold - backup |  | 1 | 0 |  | 0-0:96.61.3.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when CAT-M should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "0000603D03FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long |  |  |  | -115(dbm) |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| Telecom CATM-NBIOT switch threshold - backup |  | 1 | 0 |  | 0-0:96.61.4.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Threshold when NB-IoT should be abandoned and another comm path should be chosen
1 | logical_name | octet_string[6] |  |  |  | "0000603D04FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long |  |  |  | -125(dbm) |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| PLCG3TimeOut -backup |  | 1 | 0 |  | 0-0:94.43.10.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0AFE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | long_unsigned |  |  | 2160 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [46 empty] | This data defines the time, in minutes, after which a meter that has not been individually addressed (meaning the meter has not received any Path Discovery message, ICMP ping, nor unicast DLMS APDU) returns to the non associated state and loses its PAN coordinator. A value equal to 0 is equivalent to cancel the use of the related time-out-not-addressed counter. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 2160 (36h)
| AdpLBPAssociationSetup - backup |  | 1 | 0 |  | 0-0:94.43.14.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | This object contains parameters for Bootstrapping procedure setup - couldn't be identified in GCP "G3-PLC MAC 6LoWPAN adaptation layer setup" please DOUBLE CHECK
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0EFE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | structure { Association_max_retry: unsigned8 Association_rand_wait_time_step: unsigned8 Association_alt_PAN: boolean Join_LQI_threshold: unsigned8 Active_scan_duration: unsigned8 } |  |  |  | {8;15;1;52,15} |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [46 empty] | Association_max_retry This attribute indicates the maximum number of association retries carried out for one PAN. Authorized value: 1 to 255 Association_rand_wait_time_step This attribute indicates the waiting window time step in minutes between two associations retries for the same PAN. Authorized value : 0 to 255 Association_alt_PAN This attribute indicates whether or not the device tries to join an alternate PAN after reaching Association_max_retry retries. Authorized value : 0 : FALSE 1 : TRUE Join_LQI_threshold This attribute specifies the LQI threshold value to be used for LBA and PAN selection. Authorized value : 0 to 255 Active_scan_duration This attribute specifies the duration in seconds of the active scan. It is recommended that this attribute is greater than mac_beacon_randomization_window_length. Authorized value : 0 to 255
| MacCoherentTransmission - backup |  | 1 | 0 |  | 0-0:94.43.12.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | Indicates the coherent modulation scheme to set in the tone map response - couldn't be found in GCP, please double check and add if not standard
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0CFE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [46 empty] | value Data type: ENUMERATED Authorized values: 0 only differential modulation scheme shall be set in tone map response 1 only coherent modulations scheme shall be set in tone map response 2 Either coherent or differential scheme may be set in tone map response. Default value: 0
| macSNRdBUseDiff8PSK - backup |  | 1 | 0 |  | 0-0:94.43.13.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B0DFE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | structure of Unsigned {MAC_SNRDBROBO_ID MAC_SNRDBDBPSK_ID MAC_SNRDBDQPSK_ID MAC_SNRDBD8PSK_ID} |  |  |  | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | indicates the number of dB with respect to the macSNRdBD8PSK threshold to force the tone map algorithm to ask for differential scheme - part of mac coherent transmission | Unsigned maps to Unsigned8.
| Module system configuration - backup |  | 1 | 0 |  | 0-0:94.43.8.254 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B08FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 6 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [46 empty] | (0) Automatic. Cat-M is preferred, (1) GSM, (4) NB-Iot only (5) Cat-M only (6) Automatic. NB-Iot is preferred
| Module server configuration - backup |  | 1 | 0 |  | 0-0:96.5.2.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000600502FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | value | enum |  |  |  | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [46 empty] | enum: (0) TCP_Server, (1) UDP_Server(Default)
| G3-PLC MAC setup - pending |  | 91 | 4 |  | 0-0:29.1.0.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D010000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | mac_short_address | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | mac_RC_coord | long_unsigned |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | mac_PAN_id | long_unsigned |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
5 | mac_key_table | array |  |  | 0x20 |  |  | -- | -- | Set | Get | -- | Set | Set | -- | Set | --
6 | mac_frame_counter | double_long_unsigned |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | mac_tone_mask | bit_string |  |  | 0x30 | choice( "\111111111111111111111111111111111111000000000000000000000000000000000000", "\111111111111111111111111111111111111111111111111111111111111111111111111") |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
8 | mac_TMR_TTL | unsigned |  |  | 0x38 | 2 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
9 | mac_max_frame_retries | unsigned |  |  | 0x40 | 5 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
10 | mac_neighbour_table_entry_TTL | unsigned |  |  | 0x48 | 255 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
11 | mac_neighbour_table | array |  |  | 0x50 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | mac_high_priority_window_size | unsigned |  |  | 0x58 | 7 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
13 | mac_CSMA_fairness_limit | unsigned |  |  | 0x60 | 25 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
14 | mac_beacon_randomization_window_length | unsigned |  |  | 0x68 | 12 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
15 | mac_A | unsigned |  |  | 0x70 | 8 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
16 | mac_K | unsigned |  |  | 0x78 | 5 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
17 | mac_min_CW_attempts | unsigned |  |  | 0x80 | 10 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
18 | mac_cenelec_legacy_mode | unsigned |  |  | 0x88 | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
19 | mac_FCC_legacy_mode | unsigned |  |  | 0x90 | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
20 | mac_max_BE | unsigned |  |  | 0x98 | 8 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
21 | mac_max_CSMA_backoffs | unsigned |  |  | 0xA0 | 50 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
22 | mac_min_BE | unsigned |  |  | 0xA8 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
23 | mac_broadcast_max_CW_enabled | boolean |  |  | 0xB0 | FALSE |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
24 | mac_transmit_attn | unsigned |  |  | 0xB8 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
25 | mac_POS_table | array |  |  | 0xC0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
26 | mac_duplicate_detection_TTL | unsigned |  |  | 0xC8 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
27 | mac_POS_recent_entry_threshold | unsigned |  |  | 0xD0 | 120 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
28 | mac_POS_recent_entries | long-unsigned |  |  | 0xD8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
29 | mac_preamble_lenght | unsigned |  |  | 0xE0 | 8 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
1 | mac_get_neighbour_table_entry | long_unsigned |  |  | 0xE8 |  |  | -- | -- | Action | -- | -- | Action | Action | -- | Action | --
2 | mac_get_POS_Table_entry | long-unsigned |  |  | 0xF0 |  |  | -- | -- | Action | -- | -- | Action | Action | -- | Action | --
| G3-PLC MAC 6LoWPAN adaptation layer setup - pending |  | 92 | 4 |  | 0-0:29.2.0.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D020000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | adp_max_hops | unsigned |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
3 | adp_weak_LQI_value | unsigned |  |  | 0x10 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
4 | adp_security_level | unsigned |  |  | 0x18 | 5 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | adp_prefix_table | array |  |  | 0x20 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | adp_routing_configuration | array |  |  | 0x28 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
7 | adp_broadcast_log_table_entry_TTL | long_unsigned |  |  | 0x30 | 2 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
8 | adp_routing_table | array |  |  | 0x38 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
9 | adp_context_information_table | array |  |  | 0x40 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
10 | adp_blacklist_table | array |  |  | 0x48 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
11 | adp_broadcast_log_table | array |  |  | 0x50 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | adp_group_table | array |  |  | 0x58 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
13 | adp_max_join_wait_time | long_unsigned |  |  | 0x60 | 20 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
14 | adp_path_discovery_time | unsigned |  |  | 0x68 | 40 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
15 | adp_active_key_index | unsigned |  |  | 0x70 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
16 | adp_metric_type | unsigned |  |  | 0x78 | 0x0F |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
17 | adp_coord_short_address | long_unsigned |  |  | 0x80 | 0x0000 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
18 | adp_disable_default_routing | boolean |  |  | 0x88 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
19 | adp_device_type | enum |  |  | 0x90 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
20 | adp_default_coord_route_enabled | boolean |  |  | 0x98 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
21 | adp_destination_address_set | array |  |  | 0xA0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
22 | adp_low_LQI_value | unsigned |  |  | 0xA8 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
23 | adp_high_LQI_value | unsigned |  |  | 0xB0 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
24 | adp_delay_low_LQI | long-unsigned |  |  | 0xB8 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
25 | adp_delay_high_LQI | long-unsigned |  |  | 0xC0 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
26 | adp_RREQ_jitter_low_LQ | unsigned |  |  | 0xC8 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
27 | adp_RREQ_jitter_high_LQI | unsigned |  |  | 0xD0 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
28 | adp_trickle_data_enabled | boolean |  |  | 0xD8 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
29 | adp_trickle_LQI_threshold_low | unsigned |  |  | 0xE0 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
30 | adp_trickle_step | unsigned |  |  | 0xE8 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
31 | adp_trickle_Imin | long-unsigned |  |  | 0xF0 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
32 | adp_trickle_max_Ki | unsigned |  |  | 0xF8 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
33 | adp_trickle_adaptive_Imin | boolean |  |  | 0x100 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
34 | adp_trickle_adaptive_Ki | boolean |  |  | 0x108 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
35 | adp_cluster_trickle_enabled | boolean |  |  | 0x110 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
36 | adp_cluster_min_LQI | unsigned |  |  | 0x118 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
37 | adp_cluster_trickle_K | unsigned |  |  | 0x120 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
38 | adp_cluster_RREQ_route_cost_deviation | unsigned |  |  | 0x128 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
39 | adp_cluster_trickle_I | long-unsigned |  |  | 0x130 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
40 | adp_trickle_LQI_threshold_high | unsigned |  |  | 0x138 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| G3-PLC MAC Hybrid RF MAC setup - pending |  | 161 | 1 |  | 0-0:29.4.0.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D040000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | mac_max_BE_RF | unsigned |  |  | 0x08 | 8 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
3 | mac_max_CSMA_backoffs_RF | unsigned |  |  | 0x10 | 4 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
4 | mac_max_frame_retries_RF | unsigned |  |  | 0x18 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | mac_min_BE_RF | unsigned |  |  | 0x20 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
6 | mac_frame_counter_RF | double-long-unsigned |  |  | 0x28 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | mac_duplicate_detection_TTL_RF | unsigned |  |  | 0x30 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
8 | mac_POS_table_RF | array |  |  | 0x38 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
9 | mac_operating_mode_RF | unsigned |  |  | 0x40 | 1 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
10 | mac_channel_number_RF | long-unsigned |  |  | 0x48 | 29 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
11 | mac_duty_cycle_usage_RF | unsigned |  |  | 0x50 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | mac_duty_cycle_period_RF | long-unsigned |  |  | 0x58 | 3600 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
13 | mac_duty_cycle_limit_RF | long-unsigned |  |  | 0x60 | 90 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
14 | mac_duty_cycle_threshold_RF | unsigned |  |  | 0x68 | 90 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
15 | mac_disable_PHY_RF | boolean |  |  | 0x70 | FALSE |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
16 | mac_frequency_band_RF | enum |  |  | 0x78 | 4 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
17 | mac_transmit_atten_RF | unsigned |  |  | 0x80 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
18 | mac_adaptive_power_step_RF | unsigned |  |  | 0x88 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
19 | mac_adaptive_power_high_bound_RF | unsigned |  |  | 0x90 | 104 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
20 | mac_adaptive_power_low_bound_RF | unsigned |  |  | 0x98 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
21 | mac_POS_recent_entries_RF | long-unsigned |  |  | 0xA0 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
22 | mac_hopping_enabled_RF | boolean |  |  | 0xA8 | FALSE |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
23 | mac_broadcast_interval_duration_RF | long-unsigned |  |  | 0xB0 | 400 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
24 | mac_broadcast_slot_duration_RF | unsigned |  |  | 0xB8 | 100 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
25 | mac_unicast_slot_duration_RF | unsigned |  |  | 0xC0 | 100 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
26 | mac_extended_bitmap_RF | bit-string |  |  | 0xC8 | "\111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111" |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
27 | mac_beacon_randomization_window_length_RF | long-unsigned |  |  | 0xD0 | choice(12000,50) |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
28 | mac_additional_channel_scan_time_RF | unsigned |  |  | 0xD8 | 50 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
29 | mac_max_cca_attempts_retries_RF | unsigned |  |  | 0xE0 | 15 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
30 | mac_min_inter_Tx_interval_RF | long-unsigned |  |  | 0xE8 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
31 | mac_initial_retry_time_RF | long-unsigned |  |  | 0xF0 | 50 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
32 | mac_maximum_retry_time_RF | long-unsigned |  |  | 0xF8 | 1000 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
33 | mac_max_clock_drift_RF | unsigned |  |  | 0x100 | 20 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
34 | mac_FH_unicast_schedule_address_RF | long-unsigned |  |  | 0x108 | 0xFFFF |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
35 | mac_FH_unicast_slot_number_RF | long-unsigned |  |  | 0x110 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
36 | mac_FH_unicast_offset_RF | unsigned |  |  | 0x118 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
37 | mac_min_guard_time_RF | unsigned |  |  | 0x120 | 2 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
38 | mac_max_bcast_resync_wait_unit_RF | unsigned |  |  | 0x128 | 5 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
1 | mac_get_POS_table_entry_RF | long-unsigned |  |  | 0x130 |  |  | -- | -- | Action | -- | -- | Action | Action | -- | Action | --
| G3-PLC Hybrid 6LoWPAN adaptation layer setup - pending |  | 162 | 1 |  | 0-0:29.5.0.0 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D050000" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | adp_routing_table | array |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | adp_blacklist_table | array |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | adp_low_LQI_value_RF | unsigned |  |  | 0x18 | 75 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | -- | [45 empty] | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | adp_high_LQI_value_RF | unsigned |  |  | 0x20 | 150 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
6 | adp_routing_configuration_RF | array |  |  | 0x28 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
7 | adp_use_backup_media | boolean |  |  | 0x30 | TRUE |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
8 | adp_weak_LQI_value_RF | unsigned |  |  | 0x38 | 85 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
9 | adp_trickle_LQI_threshold_low_RF | unsigned |  |  | 0x40 | 85 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
10 | adp_delay_low_LQI_RF | long-unsigned |  |  | 0x48 | 1500 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
11 | adp_delay_high_LQI_RF | long-unsigned |  |  | 0x50 | 300 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
12 | adp_RREQ_jitter_low_LQI_RF | unsigned |  |  | 0x58 | 60 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
13 | adp_RREQ_jitter_high_LQI_RF | unsigned |  |  | 0x60 | 180 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
14 | adp_cluster_trickle_I_RF | long-unsigned |  |  | 0x68 |  |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
15 | adp_cluster_trickle_K_RF | unsigned |  |  | 0x70 | 3 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
16 | adp_cluster_min_LQI_RF | unsigned |  |  | 0x78 | 90 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
17 | 17. adp_last_gasp | boolean |  |  | 0x80 | FALSE |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
18 | adp_probing_interval | unsigned |  |  | 0x88 | 0 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
19 | adp_trickle_LQI_threshold_high_RF | unsigned |  |  | 0x90 | 95 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get, Set | -- | Get, Set | --
| G3-PLC MAC setup - backup |  | 91 | 4 |  | 0-0:29.1.0.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D0100FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | mac_short_address | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | mac_RC_coord | long_unsigned |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | mac_PAN_id | long_unsigned |  |  | 0x18 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
5 | mac_key_table | array |  |  | 0x20 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | mac_frame_counter | double_long_unsigned |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | mac_tone_mask | bit_string |  |  | 0x30 | choice( "\111111111111111111111111111111111111000000000000000000000000000000000000", "\111111111111111111111111111111111111111111111111111111111111111111111111") |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
8 | mac_TMR_TTL | unsigned |  |  | 0x38 | 2 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
9 | mac_max_frame_retries | unsigned |  |  | 0x40 | 5 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
10 | mac_neighbour_table_entry_TTL | unsigned |  |  | 0x48 | 255 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
11 | mac_neighbour_table | array |  |  | 0x50 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | mac_high_priority_window_size | unsigned |  |  | 0x58 | 7 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
13 | mac_CSMA_fairness_limit | unsigned |  |  | 0x60 | 25 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
14 | mac_beacon_randomization_window_length | unsigned |  |  | 0x68 | 12 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
15 | mac_A | unsigned |  |  | 0x70 | 8 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
16 | mac_K | unsigned |  |  | 0x78 | 5 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
17 | mac_min_CW_attempts | unsigned |  |  | 0x80 | 10 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
18 | mac_cenelec_legacy_mode | unsigned |  |  | 0x88 | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
19 | mac_FCC_legacy_mode | unsigned |  |  | 0x90 | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
20 | mac_max_BE | unsigned |  |  | 0x98 | 8 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
21 | mac_max_CSMA_backoffs | unsigned |  |  | 0xA0 | 50 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
22 | mac_min_BE | unsigned |  |  | 0xA8 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
23 | mac_broadcast_max_CW_enabled | boolean |  |  | 0xB0 | FALSE |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
24 | mac_transmit_attn | unsigned |  |  | 0xB8 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
25 | mac_POS_table | array |  |  | 0xC0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
26 | mac_duplicate_detection_TTL | unsigned |  |  | 0xC8 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
27 | mac_POS_recent_entry_threshold | unsigned |  |  | 0xD0 | 120 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
28 | mac_POS_recent_entries | long-unsigned |  |  | 0xD8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
29 | mac_preamble_lenght | unsigned |  |  | 0xE0 | 8 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
1 | mac_get_neighbour_table_entry | long_unsigned |  |  | 0xE8 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | mac_get_POS_Table_entry | long-unsigned |  |  | 0xF0 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| G3-PLC MAC 6LoWPAN adaptation layer setup - backup |  | 92 | 4 |  | 0-0:29.2.0.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D0200FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | adp_max_hops | unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | adp_weak_LQI_value | unsigned |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | adp_security_level | unsigned |  |  | 0x18 | 5 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | adp_prefix_table | array |  |  | 0x20 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | adp_routing_configuration | array |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | adp_broadcast_log_table_entry_TTL | long_unsigned |  |  | 0x30 | 2 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
8 | adp_routing_table | array |  |  | 0x38 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
9 | adp_context_information_table | array |  |  | 0x40 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
10 | adp_blacklist_table | array |  |  | 0x48 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
11 | adp_broadcast_log_table | array |  |  | 0x50 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | adp_group_table | array |  |  | 0x58 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
13 | adp_max_join_wait_time | long_unsigned |  |  | 0x60 | 20 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
14 | adp_path_discovery_time | unsigned |  |  | 0x68 | 40 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
15 | adp_active_key_index | unsigned |  |  | 0x70 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
16 | adp_metric_type | unsigned |  |  | 0x78 | 0x0F |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
17 | adp_coord_short_address | long_unsigned |  |  | 0x80 | 0x0000 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
18 | adp_disable_default_routing | boolean |  |  | 0x88 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
19 | adp_device_type | enum |  |  | 0x90 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
20 | adp_default_coord_route_enabled | boolean |  |  | 0x98 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
21 | adp_destination_address_set | array |  |  | 0xA0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
22 | adp_low_LQI_value | unsigned |  |  | 0xA8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
23 | adp_high_LQI_value | unsigned |  |  | 0xB0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
24 | adp_delay_low_LQI | long-unsigned |  |  | 0xB8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
25 | adp_delay_high_LQI | long-unsigned |  |  | 0xC0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
26 | adp_RREQ_jitter_low_LQ | unsigned |  |  | 0xC8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
27 | adp_RREQ_jitter_high_LQI | unsigned |  |  | 0xD0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
28 | adp_trickle_data_enabled | boolean |  |  | 0xD8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
29 | adp_trickle_LQI_threshold_low | unsigned |  |  | 0xE0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
30 | adp_trickle_step | unsigned |  |  | 0xE8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
31 | adp_trickle_Imin | long-unsigned |  |  | 0xF0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
32 | adp_trickle_max_Ki | unsigned |  |  | 0xF8 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
33 | adp_trickle_adaptive_Imin | boolean |  |  | 0x100 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
34 | adp_trickle_adaptive_Ki | boolean |  |  | 0x108 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
35 | adp_cluster_trickle_enabled | boolean |  |  | 0x110 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
36 | adp_cluster_min_LQI | unsigned |  |  | 0x118 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
37 | adp_cluster_trickle_K | unsigned |  |  | 0x120 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
38 | adp_cluster_RREQ_route_cost_deviation | unsigned |  |  | 0x128 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
39 | adp_cluster_trickle_I | long-unsigned |  |  | 0x130 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
40 | adp_trickle_LQI_threshold_high | unsigned |  |  | 0x138 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| G3-PLC MAC Hybrid RF MAC setup - backup |  | 161 | 1 |  | 0-0:29.4.0.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D0400FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | mac_max_BE_RF | unsigned |  |  | 0x08 | 8 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | mac_max_CSMA_backoffs_RF | unsigned |  |  | 0x10 | 4 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | mac_max_frame_retries_RF | unsigned |  |  | 0x18 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | mac_min_BE_RF | unsigned |  |  | 0x20 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | mac_frame_counter_RF | double-long-unsigned |  |  | 0x28 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | mac_duplicate_detection_TTL_RF | unsigned |  |  | 0x30 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
8 | mac_POS_table_RF | array |  |  | 0x38 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
9 | mac_operating_mode_RF | unsigned |  |  | 0x40 | 1 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
10 | mac_channel_number_RF | long-unsigned |  |  | 0x48 | 29 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
11 | mac_duty_cycle_usage_RF | unsigned |  |  | 0x50 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | mac_duty_cycle_period_RF | long-unsigned |  |  | 0x58 | 3600 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
13 | mac_duty_cycle_limit_RF | long-unsigned |  |  | 0x60 | 90 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
14 | mac_duty_cycle_threshold_RF | unsigned |  |  | 0x68 | 90 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
15 | mac_disable_PHY_RF | boolean |  |  | 0x70 | FALSE |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
16 | mac_frequency_band_RF | enum |  |  | 0x78 | 4 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
17 | mac_transmit_atten_RF | unsigned |  |  | 0x80 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
18 | mac_adaptive_power_step_RF | unsigned |  |  | 0x88 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
19 | mac_adaptive_power_high_bound_RF | unsigned |  |  | 0x90 | 104 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
20 | mac_adaptive_power_low_bound_RF | unsigned |  |  | 0x98 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
21 | mac_POS_recent_entries_RF | long-unsigned |  |  | 0xA0 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
22 | mac_hopping_enabled_RF | boolean |  |  | 0xA8 | FALSE |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
23 | mac_broadcast_interval_duration_RF | long-unsigned |  |  | 0xB0 | 400 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
24 | mac_broadcast_slot_duration_RF | unsigned |  |  | 0xB8 | 100 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
25 | mac_unicast_slot_duration_RF | unsigned |  |  | 0xC0 | 100 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
26 | mac_extended_bitmap_RF | bit-string |  |  | 0xC8 | "\111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111111" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
27 | mac_beacon_randomization_window_length_RF | long-unsigned |  |  | 0xD0 | choice(12000,50) |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
28 | mac_additional_channel_scan_time_RF | unsigned |  |  | 0xD8 | 50 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
29 | mac_max_cca_attempts_retries_RF | unsigned |  |  | 0xE0 | 15 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
30 | mac_min_inter_Tx_interval_RF | long-unsigned |  |  | 0xE8 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
31 | mac_initial_retry_time_RF | long-unsigned |  |  | 0xF0 | 50 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
32 | mac_maximum_retry_time_RF | long-unsigned |  |  | 0xF8 | 1000 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
33 | mac_max_clock_drift_RF | unsigned |  |  | 0x100 | 20 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
34 | mac_FH_unicast_schedule_address_RF | long-unsigned |  |  | 0x108 | 0xFFFF |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
35 | mac_FH_unicast_slot_number_RF | long-unsigned |  |  | 0x110 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
36 | mac_FH_unicast_offset_RF | unsigned |  |  | 0x118 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
37 | mac_min_guard_time_RF | unsigned |  |  | 0x120 | 2 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
38 | mac_max_bcast_resync_wait_unit_RF | unsigned |  |  | 0x128 | 5 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
1 | mac_get_POS_table_entry_RF | long-unsigned |  |  | 0x130 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| G3-PLC Hybrid 6LoWPAN adaptation layer setup - backup |  | 162 | 1 |  | 0-0:29.5.0.254 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00001D0500FE" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
2 | adp_routing_table | array |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
3 | adp_blacklist_table | array |  |  | 0x10 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
4 | adp_low_LQI_value_RF | unsigned |  |  | 0x18 | 75 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | keys must be defined: Shall we define defaults or add it to CTI file ?
5 | adp_high_LQI_value_RF | unsigned |  |  | 0x20 | 150 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
6 | adp_routing_configuration_RF | array |  |  | 0x28 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
7 | adp_use_backup_media | boolean |  |  | 0x30 | TRUE |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
8 | adp_weak_LQI_value_RF | unsigned |  |  | 0x38 | 85 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
9 | adp_trickle_LQI_threshold_low_RF | unsigned |  |  | 0x40 | 85 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
10 | adp_delay_low_LQI_RF | long-unsigned |  |  | 0x48 | 1500 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
11 | adp_delay_high_LQI_RF | long-unsigned |  |  | 0x50 | 300 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
12 | adp_RREQ_jitter_low_LQI_RF | unsigned |  |  | 0x58 | 60 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
13 | adp_RREQ_jitter_high_LQI_RF | unsigned |  |  | 0x60 | 180 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
14 | adp_cluster_trickle_I_RF | long-unsigned |  |  | 0x68 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
15 | adp_cluster_trickle_K_RF | unsigned |  |  | 0x70 | 3 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
16 | adp_cluster_min_LQI_RF | unsigned |  |  | 0x78 | 90 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
17 | 17. adp_last_gasp | boolean |  |  | 0x80 | FALSE |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
18 | adp_probing_interval | unsigned |  |  | 0x88 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
19 | adp_trickle_LQI_threshold_high_RF | unsigned |  |  | 0x90 | 95 |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | --
| General display readout (profiles) |  | 7 | 1 |  | 0-0:21.0.3.255 | [14 empty] | Yes | Yes | Yes | BASIC | [30 empty] | UC18
1 | logical_name | octet_string[6] |  |  |  | "0000150003FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | buffer | array[0] |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
3 | capture_objects |  |  |  | 0x10 | See Display and CII lists tab |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | no capturing
5 | sort_method | enum |  |  | 0x20 | 1 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | unsorted (FIFO)
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | not relevant
7 | entries_in_use | double_long_unsigned |  |  | 0x30 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | no data recording
8 | profile_entries | double_long_unsigned |  |  | 0x38 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | no data recording
1 | reset | integer |  |  | 0x58 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Event Object - Security Log |  | 1 | 0 |  | 0-0:96.11.7.255 | [14 empty] | Yes | Yes | Yes | BASIC | [23 empty] | UC11 |  |  |  |  | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600B07FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
2 | value | choice(enum, long_unsigned) |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
| Security Log |  | 7 | 1 |  | 0-0:99.98.7.255 | [14 empty] | Yes | Yes | Yes | BASIC | [23 empty] | UC11 |  |  |  |  | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000636207FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
2 | buffer | array |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get | [45 empty] | selective access per range
3 | capture_objects | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.7.255,2,0}} <Not Configurable remotely> |  | -- | -- | Get, | Get | Get | Get, | Get, | -- | -- | Get, | [45 empty] | clock;tamper event code
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get | [45 empty] | asynchronously
5 | sort_method | enum |  |  | 0x20 | 1 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get | [46 empty] | Note the use of sort method 2, to ensure that oldest values are retained.
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get | [45 empty] | unsorted
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
8 | profile_entries | double_long_unsigned |  |  | 0x38 | [500..*] |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | Get
1 | reset | integer |  |  | 0x58 | <Disabled> |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Time threshold: auto scroll step |  | 3 | 0 |  | 1-0:94.43.20.255 | [14 empty] | Yes | Yes | Yes | BASIC | [30 empty] | UC18
1 | logical_name | octet_string[6] |  |  |  | "01005E2B14FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 | 5 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {0,7} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Time threshold: end of manual scroll |  | 3 | 0 |  | 0-0:94.43.21.255 | [14 empty] | Yes | Yes | Yes | BASIC | [30 empty] | UC18
1 | logical_name | octet_string[6] |  |  |  | "00005E2B15FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 | 60 |  | -- | -- | Get, Set | Get | Get | Get, Set | Get, Set | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {0,7} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Null-data Control |  | 1 | 0 |  | 0-0:94.43.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [32 empty] | UC20
1 | logical_name | octet_string[6] |  |  |  | "00005E2B00FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | Boolean |  |  | 0x08 | TRUE = on, FALSE = off |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [46 empty] | Note that there will be a bit set in the APDU header to indicate whether V.44 is applied or not.
| Active firmware identifier 3 (non legally relevant/application) |  | 1 | 0 |  | 1-3:0.2.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0103000200FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware signature 3 (non legally relevant/application) |  | 1 | 0 |  | 1-3:0.2.8.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0103000208FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware identifier 4 |  | 1 | 0 |  | 1-4:0.2.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0104000200FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware signature 4 |  | 1 | 0 |  | 1-4:0.2.8.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0104000208FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware identifier 5 |  | 1 | 0 |  | 1-5:0.2.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0105000200FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware signature 5 |  | 1 | 0 |  | 1-5:0.2.8.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0105000208FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware identifier 6 |  | 1 | 0 |  | 1-6:0.2.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0106000200FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Active firmware signature 6 |  | 1 | 0 |  | 1-6:0.2.8.255 | [14 empty] | Yes | Yes | Yes | BASIC | [22 empty] | UC10
1 | logical_name | octet_string[6] |  |  |  | "0106000208FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Module system configuration |  | 1 | 0 |  | 0-0:94.43.8.255 | [14 empty] | Yes | Yes | Yes | COM | [7 empty] | CELL | [17 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B08FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | enum |  |  |  | 6 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [46 empty] | (0) Automatic. Cat-M is preferred, (1) GSM, (4) NB-Iot only (5) Cat-M only (6) Automatic. NB-Iot is preferred
| Module server configuration |  | 1 | 0 |  | 0-0:96.5.2.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "0000600502FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | enum |  |  |  | 1 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [46 empty] | enum: (0) TCP_Server, (1) UDP_Server(Default)
| Periodic ping configuration |  | 1 | 0 |  | 0-0:94.43.55.255 | [14 empty] | Yes | Yes | Yes | COM | [25 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B37FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  |  | { Ping Destination Octet string, Ping Timer long-unsigned, minutes. Num-pings long-unsigned, (range 1-100) Multiplication_factor long-unsigned, (range 1-100) Number_of_retries long-unsigned, (range 1-100) } |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | enum: (0) TCP_Server, (1) UDP_Server(Default)
| PHY randomization |  | 1 | 0 |  | 0-0:94.43.56.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B38FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | structure |  |  |  | {240;2;6;1} |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [46 empty] | Value ::= structure { randomisation_start_window double-long-unsigned, multiplication_factor long-unsigned, number_of_retries long-unsigned, direct_attach_at_power_on_flag boolean, }
| Network status check timer |  | 1 | 0 |  | 0-0:94.43.57.255 | [14 empty] | Yes | Yes | Yes | COM | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B39FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  |  | 6 |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [46 empty] | Time in minutes for the comms element to re-check the network attach status. If set to 0xFFFF then the timer is disabled.
| Network condition profille |  | 7 | 1 |  | 0-0:99.12.0.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000630C00FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
2 | buffer | array[0] |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | --
3 | capture_objects |  |  |  | 0x10 | { {8,0-0:1.0.0.255,2,0} - Clock {1,0-0:25.6.0.255,3,0} - GSM diagnostic/ status {1,0-0:25.6.0.255,5,0} - GSM diagnostic/ ps_status {1,0-0:25.6.0.255,6,0} - GSM diagnostic/ cell_info {1,0-0:25.6.0.255,8,0} - GSM diagnostic/ capture_time {1,0-1:94.43.4.255,2,8} - Network Information/ PCI {1,0-1:94.43.4.255,2,9} - Network Information/ EARFNC {1,0-1:94.43.4.255,2,10} - Network Information/ TAC {1,0-0:25.11.0.255,2,0} - LTE Monitoring/ LTE_network_parameters {1,0-0:25.11.0.255,3,0} - LTE Monitoring/ LTE_quality_of_service } |  | -- | -- | Get, Set | -- | -- | Get, Set | Get | -- | -- | --
4 | capture_period | double_long_unsigned |  |  | 0x18 | 600 |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | -- | [45 empty] | no capturing
5 | sort_method | enum |  |  | 0x20 | 1 |  | -- | -- | (Get) | -- | -- | (Get) | (Get) | -- | -- | -- | [45 empty] | unsorted (FIFO)
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | (Get) | -- | -- | (Get) | (Get) | -- | -- | -- | [45 empty] | not relevant
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | (Get) | -- | -- | (Get) | (Get) | -- | -- | -- | [45 empty] | no data recording
8 | profile_entries | double_long_unsigned |  |  | 0x38 | 60 |  | -- | -- | (Get) | -- | -- | (Get) | (Get) | -- | -- | -- | [45 empty] | no data recording
1 | reset | integer |  |  | 0x58 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Event Object - PDP context error code |  | 1 | 0 |  | 0-0:96.11.9.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13 |  |  | UC16
1 | logical_name | octet_string[6] |  |  |  | "0000600B09FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | value | choice(enum, long_unsigned) |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
| PDP context error code log |  | 7 | 1 |  | 0-0:99.98.9.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13 |  |  | UC16
1 | logical_name | octet_string[6] |  |  |  | "0000636209FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
2 | buffer | array |  |  | 0x08 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | selective access per range
3 | capture_objects | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.9.255,2,0}} |  | -- | -- | Get, Set | Get | -- | Get, Set | Get | -- | -- | -- | [45 empty] | clock;tamper event code
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | asynchronously
5 | sort_method | enum |  |  | 0x20 | 2 |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [46 empty] | Note the use of sort method 2, to ensure that oldest values are retained.
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | -- | [45 empty] | unsorted
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
8 | profile_entries | double_long_unsigned |  |  | 0x38 | [500..*] |  | -- | -- | Get | Get | -- | Get | Get | -- | -- | --
1 | reset | integer |  |  | 0x58 | <Disabled> |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
| Bytes sent in an interval - Counter |  | 1 | 0 |  | 0-0:96.12.132.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000600C84FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Bytes received in an interval - Counter |  | 1 | 0 |  | 0-0:96.12.133.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000600C85FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | double_long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Bytes sent total counter |  | 1 | 0 |  | 0-0:96.12.134.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000600C86FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long64_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Bytes received total counter |  | 1 | 0 |  | 0-0:96.12.135.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000600C87FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long64_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
| Comms throughput counter profile |  | 7 | 1 |  | 0-0:99.12.1.255 | [14 empty] | Yes | Yes | Yes | BASIC | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "0000630C01FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | buffer | array |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | selective access per range
3 | capture_objects | array[2](capture_object_definition) |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.12.132.255,2,0}, {1,0-0:96.12.133.255,2,0}} |  | -- | -- | Get, (Set) | Get | Get | Get, (Set) | Get, (Set) | -- | -- | -- | [45 empty] | clock;tamper event code
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | asynchronously
5 | sort_method | enum |  |  | 0x20 | 2 |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [46 empty] | Note the use of sort method 2, to ensure that oldest values are retained.
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | -- | [45 empty] | unsorted
7 | entries_in_use | double_long_unsigned |  |  | 0x30 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
8 | profile_entries | double_long_unsigned |  |  | 0x38 | [500..*] |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset | integer |  |  | 0x58 | <Disabled> |  | -- | -- | Action | -- | -- | Action | -- | -- | -- | --
| PLCG3_Bandplan - Active |  | 1 | 0 |  | 0-0:94.43.128.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B80FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | This object allows the identification of the current bandplan in use. The supported bandplans are 0 = Only CENELEC-A band 3 = Only FCC band Default value: 3 Switching between Cenelec A and FCC band must be possible by configuration change: This object shall be declared as readable and writable and allows changing the current bandplan in use.
| PLCG3_Bandplan - Pending |  | 1 | 0 |  | 0-0:94.43.128.0 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8000" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [46 empty] | This object allows the identification of the current bandplan in use. The supported bandplans are 0 = Only CENELEC-A band 3 = Only FCC band Default value: 3 Switching between Cenelec A and FCC band must be possible by configuration change: This object shall be declared as readable and writable and allows changing the current bandplan in use.
| PLCG3_Bandplan - Backup |  | 1 | 0 |  | 0-0:94.43.128.254 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B80FE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [46 empty] | This object allows the identification of the current bandplan in use. The supported bandplans are 0 = Only CENELEC-A band 3 = Only FCC band Default value: 3 Switching between Cenelec A and FCC band must be possible by configuration change: This object shall be declared as readable and writable and allows changing the current bandplan in use.
| G3 MAC Device Table |  | 1 | 0 |  | 0-0:94.43.17.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B11FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [46 empty] | This object describes a table of Device-Descriptor entries, for frames received over PLC. PANId The PANId of the device. Data type: UNSIGNED16 Authorized values: 0x0000 to 0xFFFF Short_address The 16-bit short address of the device. Data type: UNSIGNED16 Authorized values: 0x0000 to 0x7FFF Frame_counter The incoming 32-bit frame counter of the device. Data type: UNSIGNED32 Authorized values: 0x00000000 to 0xFFFFFFFFF array[250] (mac_device) mac_device ::= structure { PANId Short_address Frame_counter }
| G3 MAC Device Table RF |  | 1 | 0 |  | 0-0:94.43.18.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B12FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [46 empty] | This object describes a table of Device-Descriptor entries, for frames received over PLC. PANId The PANId of the device. Data type: UNSIGNED16 Authorized values: 0x0000 to 0xFFFF Short_address The 16-bit short address of the device. Data type: UNSIGNED16 Authorized values: 0x0000 to 0x7FFF Frame_counter The incoming 32-bit frame counter of the device. Data type: UNSIGNED32 Authorized values: 0x00000000 to 0xFFFFFFFFF array[250] (mac_device) mac_device ::= structure { PANId Short_address Frame_counter }
| G3 PAN connection status |  | 1 | 0 |  | 0-0:94.43.131.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B83FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [46 empty] | This object contains the network status information for the connection of the end device to the PAN coordinator. The connection status information is based on the - Routing table entry of the ‘PAN coordinator’ and - Neighbour table entry of the ‘Next Hop’ If an entry is missing or not valid, the valid_time (routing entry) or neighbour_valid_time (neighbor entry) fields is set to 0, the values for other fields are undefined. PAN_connection_status ::= structure { routing_table_entry ::= structure; neighbour_table_entry ::= structure } routing table entry to PAN coordinator routing_table_entry ::= structure { destination_address: long-unsigned, next_hop_address: long-unsigned, route_cost: long-unsigned, hop_count: unsigned, weak_link_count: unsigned, valid_time: long-unsigned } neighbor table entry of next hop neighbour_table_entry ::= structure { short_address: long-unsigned, payload_modulation_scheme: boolean, tone_map: bit-string, modulation: enum, tx_gain: integer, tx_res: enum, tx_coeff: bit-string, lqi: unsigned, phase_differential integer, TMR_valid_time: unsigned, neighbour_valid_time: unsigned }
| G3 PAN connection status profile |  | 7 | 1 |  | 0-0:94.43.132.255 | [14 empty] | Yes | Yes | Yes | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B84FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | buffer | array[0] |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
3 | capture_objects |  |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:94.43.131.255,2,0}} |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
4 | capture_period | double_long_unsigned |  |  | 0x18 | 3600, options 60,300,600,900,86400. |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | no capturing
5 | sort_method | enum |  |  | 0x20 | 1 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | unsorted (FIFO)
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | not relevant
7 | entries_in_use | double_long_unsigned |  |  | 0x30 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | no data recording
8 | profile_entries | double_long_unsigned |  |  | 0x38 | 168 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | no data recording
1 | reset | integer |  |  | 0x58 |  |  | -- | -- | Action | -- | -- | Action | -- | -- | Action | --
| G3 Alternate PAN ID |  | 1 | 0 |  | 0-0:94.43.55.255 | [14 empty] | M | M | M | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B37FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [46 empty] | This object stores the detected PANid for capturing into the AlternatePANIdLog The data contains the alternate PAN Id that has been indicated by the MLME-COMM-STATUS.indication with Status = ALTERNATE_PANID_DETECTION received from the PLC MAC layer. Only G3 neighbouring networks detected by PLC crosstalk are captured by this object. Detection of G3 neighbouring networks over radio is normal during G3 operation, so they should not be logged.
| G3 Alternate PAN ID log |  | 7 | 1 |  | 0-0:94.43.9.255 | [14 empty] | Yes | Yes | Yes | BASIC | [6 empty] | G3-PLC | [18 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | This object logs the « alternate PAN Id » detected by the meter. Everytime the MLME-COMM-STATUS.indication primitive is called with Status = ALTERNATE_PANID_DETECTION, the meter checks if there is already an entry with the same PAN-ID in the buffer: • If it is the case, this entry is updated with the current date and time, and moved to the end of the buffer (i.e. it becomes the latest element of the array); • If not, a new entry is added with the alternate PAN-Id value and the current date and time. When the buffer is full, the oldest entry is deleted to allow the storage of a new entry.
1 | logical_name | octet_string[6] |  |  |  | "00005E2B09FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | buffer | array[0] |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
3 | capture_objects |  |  |  | 0x10 | {{8,0-0:1.0.0.255,2,0}, {1,0-0:94.43.55.255,2,0}} |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | --
4 | capture_period | double_long_unsigned |  |  | 0x18 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | no capturing
5 | sort_method | enum |  |  | 0x20 | 1 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | unsorted (FIFO)
6 | sort_object | capture_object_definition |  |  | 0x28 | {*,*-*:*.*.*.*,*,*} |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | not relevant
7 | entries_in_use | double_long_unsigned |  |  | 0x30 | 0 |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | no data recording
8 | profile_entries | double_long_unsigned |  |  | 0x38 | {5..*} |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | no data recording
1 | reset | integer |  |  | 0x58 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Ethernet configuration - current |  | 1 | 0 |  | 0-0:94.43.140.255 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8CFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | See comments |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | Structure {MTU (long-unsigned),Speed (enum),DuplexMode (enum), VLANID (long-unsigned), status_led (enum), ethernet_enabled (enum)}; | See Ethernet object structures tab for details
| Ethernet filter - current |  | 1 | 0 |  | 0-0:94.43.141.255 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8DFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | See comments |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | Structure {Drop_Multicast (enum); Drop_Broadcast (enum); Drop_DHCP_req (enum); Drop_ARP (enum); ACL_MAC (array-MAC);ACL_IP (array-Subnet)} | See Ethernet object structures tab for details
| Ethernet status |  | 1 | 0 |  | 0-0:94.43.142.255 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8EFF" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | see comments |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | Structure {Ethernet_port_status (enum), speed (enum), Duplexmode (enum)}; | See Ethernet object structures tab for details
| Network Information |  | 1 | 0 |  | 0-0:94.43.150.255 | [12 empty] | M | M | M | M | M | COM | [25 empty] | UC13
1 | logical_name | octet_string[6] |  |  |  | "00005E2B96FF" |  | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [14 empty] | CELL
2 | value | struct{ IMSI octet string, IMEI octet string, MSISDN octet string, ICCID octet string, PCI long-unsigned, EARFCN double-long-unsigned, TAC long-unsigned, } | [5 empty] | -- | -- | Get | Get | -- | Get | Get | -- | Get | -- | [45 empty] | The moderm information description of present modem status. Value ::= structure { signal_strength integer, bit_error_rate integer, number_of_base_stations integer, IMSI octet string, IMEI octet string, MSISDN octet string, ICCID octet string, Main_Cell_ID double-long-unsigned, }
| Ethernet configuration - pending |  | 1 | 0 |  | 0-0:94.43.140.0 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8C00" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | See comments |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | Structure {MTU (long-unsigned),Speed (enum),DuplexMode (enum), VLANID (long-unsigned), status_led (enum), ethernet_enabled (enum)}; | See Ethernet object structures tab for details
| Ethernet filter - pending |  | 1 | 0 |  | 0-0:94.43.141.0 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8D00" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | See comments |  | -- | -- | Get, Set | Get | Get | Get, Set | Get | -- | Get, Set | -- | [45 empty] | Structure {Drop_Multicast (enum); Drop_Broadcast (enum); Drop_DHCP_req (enum); Drop_ARP (enum); ACL_MAC (array-MAC);ACL_IP (array-Subnet)} | See Ethernet object structures tab for details
| Ethernet configuration - backup |  | 1 | 0 |  | 0-0:94.43.140.254 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8CFE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | See comments |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | Structure {MTU (long-unsigned),Speed (enum),DuplexMode (enum), VLANID (long-unsigned), status_led (enum), ethernet_enabled (enum)}; | See Ethernet object structures tab for details
| Ethernet filter - backup |  | 1 | 0 |  | 0-0:94.43.141.254 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8DFE" |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | --
2 | value | structure |  |  | 0x08 | See comments |  | -- | -- | Get | Get | Get | Get | Get | -- | Get | -- | [45 empty] | Structure {Drop_Multicast (enum); Drop_Broadcast (enum); Drop_DHCP_req (enum); Drop_ARP (enum); ACL_MAC (array-MAC);ACL_IP (array-Subnet)} | See Ethernet object structures tab for details
| Ethernet module diagnostic |  | 1 | 0 |  | 0-0:94.43.143.255 | [14 empty] | M | M | M | BASIC | [11 empty] | ETH | [13 empty] | UC13 | [8 empty] | UC-Oe-01 |  |  |  |  | This contains a string received from the modem in response to the modem command string write.
1 | logical_name | octet_string[6] |  |  |  | "00005E2B8FFF" |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Security Event Counter 1 |  | 1 | 0 |  | 0-0:96.15.21.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F15FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 2 |  | 1 | 0 |  | 0-0:96.15.22.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F16FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 3 |  | 1 | 0 |  | 0-0:96.15.23.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F17FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 4 |  | 1 | 0 |  | 0-0:96.15.24.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F18FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 5 |  | 1 | 0 |  | 0-0:96.15.25.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F19FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 6 |  | 1 | 0 |  | 0-0:96.15.26.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F1AFF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 7 |  | 1 | 0 |  | 0-0:96.15.27.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F1BFF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 8 |  | 1 | 0 |  | 0-0:96.15.28.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F1CFF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 9 |  | 1 | 0 |  | 0-0:96.15.29.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F1DFF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 10 |  | 1 | 0 |  | 0-0:96.15.30.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F1EFF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 11 |  | 1 | 0 |  | 0-0:96.15.31.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F1FFF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Security Event Counter 12 |  | 1 | 0 |  | 0-0:96.15.32.255 | [14 empty] | M | M | M | BASIC | [28 empty] | UC16 |  |  |  | UC20
1 | logical_name | octet_string[6] |  |  |  | "0000600F20FF" |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
2 | value | octet_string |  |  | 0x08 |  |  | -- | -- | Get | -- | -- | Get | Get | -- | -- | Get
| Average Power factor (+A/+VA) |  | 3 | 0 |  | 1-0:13.24.0.255 | [12 empty] | O | O | O | O | O | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "01000D1800FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Average Power factor L1 (+A/+VA) |  | 3 | 0 |  | 1-0:33.24.0.255 | [12 empty] | O | O | O | O | O | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100211800FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Average Power factor L1 (+A/+VA) |  | 3 | 0 |  | 1-0:53.24.0.255 | [12 empty] | O | O | O | O | O | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100351800FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
| Average Power factor L1 (+A/+VA) |  | 3 | 0 |  | 1-0:73.24.0.255 | [12 empty] | O | O | O | O | O | BASIC | [20 empty] | UC8
1 | logical_name | octet_string[6] |  |  |  | "0100491800FF" |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
2 | value | long_unsigned |  |  | 0x08 |  |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
3 | scaler_unit | scal_unit_type |  |  | 0x10 | {-3,255} |  | -- | -- | Get | Get | Get | Get | Get | -- | -- | --
1 | reset |  |  |  | 0x28 |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Note on K48: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Security Setup Objects will have the same config, but guidance needed from the steering group.
Note on N54: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Additional rights to the other SS objects needed.
Note on O629: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Martin B to take to Christoph/ Steering
Note on B1352: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1365: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1378: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1391: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1404: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1417: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B1712: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Same as billing period log. Antwort: Take comment from the unlocked document re LP objects.
Note on B1967: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B2004: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B2041: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on B2108: L+G: Done over script "MDI reset" for all instances at the same time. MD reset per instance not supported!
Note on Q3756: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Should this be set?
Note on Q3764: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Should this be set?
Note on B4041: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Are these already managed in the G3-PLC protocol?

## Use Cases
Use Cases
ID | Use Case | Description | Comment | Gx role 1 | Gx role 2 | Gx role 3 | C | SZ role 1 | SZ role 2 | H1
UC1 | Meter Registration | Process of incorporating devices (E-meters, submeters, ...) into the system. | Maintenance and Installation client to trigger on_Installation() via HHU | management |  |  |  | maintenance
UC2 | Remote (& local) Tariff Programming | Process of remotely programming the parameters necessary to support a time of use (TOU) based tariff contract. |  | management |  |  |  | maintenance | certification
UC3 | On Demand Meter Register reading for multi-utility meters | Process of spontaneously collecting meter register readings upon a specific request. |  | management | data readout |  |  | maintenance | certification
UC4 | On Demand Meter Load Profile reading for multi-utility meters | Process of spontaneously collecting load profile register readings upon a specific request. |  | management | data readout |  |  | maintenance | certification
UC5 | Periodic Meter reading for multi-utility meters | Process of periodically collecting meter readings for billing purposes (periodic reading). |  | management | data readout |  | readout_gw
UC6 | Remote or local Disconnection and Reconnection (E, G) | Process of disconnecting or reconnecting the electricity I or gas (G) supply of a customer. |  | management |  |  |  | maintenance
UC7 | Clock Synchronization | Process of adjusting the internal clock of the metering equipment. |  | management |  |  |  | maintenance
UC8 | Quality of Supply | Process of supervising Power Outages, Sags and Swells, |  | management | data readout |  | readout_gw | maintenance
UC9 | Load Management by relay (E only) | Process of controlling specific local loads by means of relays. |  | management |  |  |  | maintenance
UC10 | Firmware update | Process of downloading new firmware to a device |  | management |  |  | fw upload | maintenance
UC11 | Meter supervision | Process of supervising any events which could comprise the meter and the system. |  | management |  |  |  | maintenance
UC12 | Consumer Information | Process of periodically transmitting meter reads and consumer information via a local digital interface. |  | management |  |  |  | maintenance |  | customer
UC13 | Communication Supervision | Process of supervising events affecting the meter to HES communication. |  | management | data readout |  |  | maintenance
UC14 | Enabling / disabling functionalities | This use case is used to enable or disable functionalities using Function control interface class objects (class 122). |  | management |  |  |  | maintenance | certification
UC15 | Power Control | Process of activating or deactivating the demanded power control mode in meters. |  | management |  |  |  | maintenance
UC16 | Alarm and event Management | Process of management of events and equipment alarms. |  | management | data readout | pre-established |  | maintenance
UC17 | Meter Availability Control | Ping a meter to check that communication works. |  | public |  |  |  | public
UC18 | Display messages on meter display | Display pre-defined or on-the-fly messages such as supply of energy or tariffs. |  | management |  |  |  | maintenance | certification
UC19 | Configuration of meter locally | This is used during initial installation or in-service control. | [5 empty] | maintenance
UC20 | Manage security settings | Setting and updating security credentials can be done remotely and cover setting new security keys or certificates in the meter. |  | security officer | public | management | public | public
UC21 | Prepayment
UcOe-01 | Communications configuration | Configuration of communications parameters needed for PLC and P2P technologies. |  | management |  |  |  | maintenance
UC Oe-02 | Calibration & maintenance | [6 empty] | maintenance | certification
UC Oe-03 | Communications Module exchange | (Open on Roles) |  | management |  |  |  | maintenance

## Power Quality Profile
Power Quality Profile |  | 1-0:99.14.0.255 | capture_period | choice(600,900)
Attributes possible for capture list |  |  | profile entries | 1440 (10min 10 days)
{8,0-0:1.0.0.255,2,0}, | 1 | Date | integration periode | 1 sec
{1,0-0:96.10.4.255,2,0}, | 2 | Status
{3,1-0:32.24.0.255,2,0}, | 3 | Average voltage L1
{3,1-0:52.24.0.255,2,0}, | 4 | Average voltage L2
{3,1-0:72.24.0.255,2,0}, | 5 | Average voltage L3
{3,1-0:32.23.0.255,2,0}, | 6 | Min voltage L1
{3,1-0:52.23.0.255,2,0}, | 7 | Min voltage L2
{3,1-0:72.23.0.255,2,0}, | 8 | Min voltage L3
{3,1-0:32.26.0.255,2,0}, | 9 | Max voltage L1
{3,1-0:52.26.0.255,2,0}, | 10 | Max voltage L2
{3,1-0:72.26.0.255,2,0}, | 11 | Max voltage L3
{3,1-0:31.24.0.255,2,0}, | 12 | Iaverage L1
{3,1-0:51.24.0.255,2,0}, | 13 | Iaverage L2
{3,1-0:71.24.0.255,2,0}, | 14 | Iaverage L3
{3,1-0:31.26.0.255,2,0}, | 15 | Imax L1
{3,1-0:51.26.0.255,2,0}, | 16 | Imax L2
{3,1-0:71.26.0.255,2,0}, | 17 | Imax L3
{3,1-0:1.24.0.255,2,0}, | 18 | Average import power
{3,1-0:16.24.0.255,2,0}, | 19 | Average Net Power (¦+A¦-¦-A¦)
{3,1-0:15.24.0.255,2,0}, | 20 | Average Total Power (¦+A¦+¦-A¦)
{3,1-0:13.24.0.255,2,0}, | 21 | Average Power factor (+A/+VA)
{3,1-0:33.24.0.255,2,0}, | 22 | Average PF L1
{3,1-0:53.24.0.255,2,0}, | 23 | Average PF L2
{3,1-0:73.24.0.255,2,0}, | 24 | Average PF L3
{3,1-0:33.23.0.255,2,0}, | 25 | Min PF L1
{3,1-0:53.23.0.255,2,0}, | 26 | Min PF L2
{3,1-0:73.23.0.255,2,0}, | 27 | Min PF L3
{1,0-0:96.7.21.255,2,0}, | 28 | number of power fails
{1,0-0:96.7.9.255,2,0}, | 29 | number of long power fails
{1,0-0:32.32.0.255,2,0}, | 30 | number of sags L1
{1,0-0:52.32.0.255,2,0}, | 31 | number of sags L2
{1,0-0:72.32.0.255,2,0}, | 32 | number of sags L3
{3,1-0:32.34.0.255,2,0}, | 33 | magnitude of sag L1
{3,1-0:52.34.0.255,2,0}, | 34 | magnitude of sag L2
{3,1-0:72.34.0.255,2,0}, | 35 | magnitude of sag L3
{3,1-0:32.33.0.255,2,0}, | 36 | duration of sag L1
{3,1-0:52.33.0.255,2,0}, | 37 | duration of sag L2
{3,1-0:72.33.0.255,2,0}, | 38 | duration of sag L3
{1,0-0:32.36.0.255,2,0}, | 39 | number of swells L1
{1,0-0:52.36.0.255,2,0}, | 40 | number of swells L2
{1,0-0:72.36.0.255,2,0}, | 41 | number of swells L3
{3,1-0:32.38.0.255,2,0}, | 42 | magnitude of swell L1
{3,1-0:52.38.0.255,2,0}, | 43 | magnitude of swell L2
{3,1-0:72.38.0.255,2,0}, | 44 | magnitude of swell L3
{3,1-0:32.37.0.255,2,0}, | 45 | duration of swell L1
{3,1-0:52.37.0.255,2,0}, | 46 | duration of swell L2
{3,1-0:72.37.0.255,2,0}, | 47 | duration of swell L3
Note. Use of Power and Current values may need Data Protection Impact Assessment.

## Events
Event definitions and assignments
[5 empty] | Logs | [12 empty] | Options |  |  | Notes
Number | Hex | Name | Description | not required for Oe | Standard Event Log | Fraud Detection Log | Disconnector Control Log | M-Bus Event Log | M-Bus Control Log 1 | M-Bus Control Log 2 | M-Bus Control Log 3 | M-Bus Control Log 4 | Power Quality Event Log | Communication Log | Communication Details Log | Certification Log | Security Log | GCP Mandatory/Optional | Oe- Mandatory/Optiona | Extensions | Oe - notes | Global event counter? | Billing event counter? | Security event counter number | Oe Requirement | Commentary
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 5
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 5
[5 empty] | x | [12 empty] | M | M
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 3
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 3
[5 empty] | x | [12 empty] | M | M
|  |  |  | ? | x | [12 empty] | O | D | [6 empty] | Note that these may be used to refer to a internal power store (e.g. supercap)
|  |  |  | ? | x | [12 empty] | O | D
[5 empty] | x | [12 empty] | M | M
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 6
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 6
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 7
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 7
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 7
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 5
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 7
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 2
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 2
[5 empty] | x | [12 empty] | M | M
|  |  |  | 1 | x | [12 empty] | O | D
[5 empty] | x | [12 empty] | O | M
[5 empty] | x | [12 empty] | M | M
[5 empty] | x | [12 empty] | M | M
24 | 18 | Communications module removed | the WAN communications module that is field-exchangeable has been removed | [11 empty] | x |  |  |  | O |  | Mandatory on meters with exchangeable comms modules
25 | 19 | Communications module fitted | a WAN communications module that is field-exchangeable has been installed | [11 empty] | x |  |  |  | O |  | Mandatory on meters with exchangeable comms modules
[15 empty] | x |  | x | M | M |  |  |  |  | 1
[15 empty] | x |  | x | M | M |  |  |  |  | 1
[15 empty] | x |  | x | M | M |  |  |  |  | 1
[15 empty] | x |  | x | M | M |  |  |  |  | 1
|  |  |  | 1 |  |  |  |  | x | [8 empty] | M | D | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | M | D | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | M | D | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | M | D | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | M | D | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | M | D | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | M | D | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [8 empty] | x | M | D | M
|  |  |  | 1 |  |  |  | x | [8 empty] | x | M | D | M
[6 empty] | x | [10 empty] | x | O | M |  | Mandatory |  |  | 4
[6 empty] | x | [10 empty] | x | O | M |  | Mandatory |  |  | 4
[6 empty] | x | [10 empty] | x | O | M |  | Mandatory - defined at 380 mT threshold |  |  | 4
[6 empty] | x | [10 empty] | x | O | M |  | Mandatory |  |  | 4
[6 empty] | x | [10 empty] | x | O | O |  |  |  |  | 4
[6 empty] | x | [10 empty] | x | O | O |  |  |  |  | 4
[6 empty] | x | [10 empty] | x | M | M |  | n=1 |  |  | 1
[5 empty] | x | [12 empty] | M | M |  | floods event log. Leave in standard only, under discussion, possibly new event log to capture this? |  |  |  | this shall only record a parameter change where no other event is generated.
[5 empty] | x | X | [10 empty] | x | M | M |  | Add cert to this or as a separate event |  |  | 8
[6 empty] | x | [10 empty] | x | M | M |  |  |  |  | 7
[6 empty] | x | [10 empty] | x | M | M |  |  |  |  | 7 | one definition is Receive DLMS frame counter value less to the last successfully received frame counter in the received APDU or received DLMS frame counter consecutive received x times (configurable with 0-0:94.43.151.255). Event signalizes as well the situation when the DC has lost the frame counter synchronization.
[5 empty] | x | [11 empty] | x | M | M |  |  |  |  | 2
[5 empty] | x | [12 empty] | O | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D | note that Breaker and Disconnector are the same. |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 10
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 10
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 10
[7 empty] | x | [9 empty] | x | O | M | D |  |  |  | 9
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[7 empty] | x | [10 empty] | M | M | L | [5 empty] | Current is used rather than fuse, this is a change in the next version of the GCP.
[7 empty] | x | [10 empty] | M | M | L
[7 empty] | x | [10 empty] | M | M | L
[7 empty] | x | [10 empty] | M | M | L
[7 empty] | x | [10 empty] | M | M | L
[7 empty] | x | [10 empty] | M | M | L
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[13 empty] | x |  |  |  |  | M | M
[5 empty] | x | [12 empty] | O | M
[5 empty] | x | [12 empty] | O | M
|  |  |  | ? | [8 empty] | x |  |  |  |  | O | D | [5 empty] | Not required
|  |  |  | 1 | [13 empty] | O | D
|  |  |  | 1 | [8 empty] | x |  |  |  |  | O | D
|  |  |  | 1 | [8 empty] | x |  |  |  |  | O | D
|  |  |  | 1 | [8 empty] | x |  |  |  |  | O | D
[7 empty] | x | [9 empty] | x | M | M |  |  |  |  | 9 |  | If I was sticking to the IEC standards, this is a Supply Control Switch (SCS)
[7 empty] | x | [9 empty] | x | M | M | D |  |  |  | 9
[5 empty] | x | [11 empty] | x | M | M | L |  |  |  | 12
[5 empty] | x | [11 empty] | x | M | M | L |  |  |  | 12
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
[5 empty] | x | [12 empty] | M | D
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
[5 empty] | x | [12 empty] | M | M
[5 empty] | x | [12 empty] | M | M
[5 empty] | x | [12 empty] | M | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 | [13 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
|  |  |  | 1 |  |  |  | x | [9 empty] | M | D | M
[14 empty] | x |  |  |  | O | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  | x | M | M |  |  |  |  | 5
[14 empty] | x |  |  | x | O | M |  |  |  |  | 5
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | M | M | [6 empty] | Test of this is not possible, if the meter is configured to reject all incoming call attempts.
|  |  |  | 1 | [9 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | O | M
[14 empty] | x |  |  |  | M | M
[14 empty] | x |  |  |  | O | M
[14 empty] | x |  |  |  | M | M | [6 empty] | I don't think we will use this mode in auto answer,
[14 empty] | x |  |  |  | O | M
159 | 9F | ping response not received start | ping has not received a response | [10 empty] | x |  |  |  |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | O |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | O |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | M |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | M |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | O |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | M |  | M
|  |  |  | 1 |  |  |  |  | x | [8 empty] | M |  | M
[14 empty] | x |  |  |  |  | M
[14 empty] | X |  |  |  |  | M
[14 empty] | x |  |  |  |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | O |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | O |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | M |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | M |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | O |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | M |  | M
|  |  |  | 1 | [5 empty] | x | [7 empty] | M |  | M
[14 empty] | x |  |  |  |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | O |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | O |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | M |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | M |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | O |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | M |  | M
|  |  |  | 1 | [6 empty] | x | [6 empty] | M |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | O |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | O |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | M |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | M |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | O |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | M |  | M
|  |  |  | 1 | [7 empty] | x | [5 empty] | M |  | M
[6 empty] | X | [9 empty] | x |  |  | M
X
202 | CA | LED pulse rate not default (TBC) | the LED pulse rate has been set to a value other than the predetermined value | [12 empty] | x |  |  | M
203 | CB | LED pulse rate returned to default (TBC) | the LED pulse rate has been re-set to the predetermined value | [12 empty] | x |  |  | M
204 | CC | Limiter 1 import activated | Indicates that the limiter has been activated |  |  |  | x | [11 empty] | M | D+L | [5 empty] | May be helpful to discuss their purpose, whether they are needed.
205 | CD | Limiter 1 import deactivated | Indicates that the limiter has been deactivated |  |  |  | x | [11 empty] | M | D+L
206 | CE | Limiter 2 import activated | Indicates that the limiter has been activated |  |  |  | x | [11 empty] | M | D+L
207 | CF | Limiter 2 import deactivated | Indicates that the limiter has been deactivated |  |  |  | x | [11 empty] | M | D+L
208 | D0 | Limiter 2 import threshold exceeded | Indicates that the limiter threshold has been exceeded. |  |  |  | x | [11 empty] | M | D+L
209 | D1 | Limiter 2 import threshold ok | Indicates that the monitored value of the limiter dropped below the threshold. |  |  |  | x | [11 empty] | M | D+L
210 | D2 | Limiter 2 import threshold changed | Indicates that the limiter threshold has been changed |  |  |  | x | [11 empty] | M | D+L
211 | D3 | Limiter 1 export activated | Indicates that the limiter has been activated |  |  |  | x | [11 empty] | M | D+L
212 | D4 | Limiter 1 export deactivated | Indicates that the limiter has been deactivated |  |  |  | x | [11 empty] | M | D+L
213 | D5 | Limiter 1 export threshold exceeded | Indicates that the limiter threshold has been exceeded. |  |  |  | x | [11 empty] | M | D+L
214 | D6 | Limiter 1 export threshold ok | Indicates that the monitored value of the limiter dropped below the threshold. |  |  |  | x | [11 empty] | M | D+L
215 | D7 | Limiter 1 export threshold changed | Indicates that the limiter threshold has been changed |  |  |  | x | [11 empty] | M | D+L
216 | D8 | Limiter 2 export activated | Indicates that the limiter has been activated |  |  |  | x | [11 empty] | M | D+L
217 | D9 | Limiter 2 export deactivated | Indicates that the limiter has been deactivated |  |  |  | x | [11 empty] | M | D+L
218 | DA | Limiter 2 export threshold exceeded | Indicates that the limiter threshold has been exceeded. |  |  |  | x | [11 empty] | M | D+L
219 | DB | Limiter 2 export threshold ok | Indicates that the monitored value of the limiter dropped below the threshold. |  |  |  | x | [11 empty] | M | D+L
220 | DC | Limiter 2 export threshold changed | Indicates that the limiter threshold has been changed |  |  |  | x | [11 empty] | M | D+L
221 | DD | Customer Interface (H1) activated | Customer Interface (H1) has been activated |  | x | [13 empty] | M
222 | DE | Customer Interface (H1) deactivated | Customer Interface (H1) has been deactivated |  | x | [13 empty] | M
223 | DF | current but no voltage L1 (CT/VT only) | Indicates that there is a current but no voltage on L1 (CT/VT only) | [9 empty] | x | [5 empty] | M
224 | E0 | current but no voltage L2 (CT/VT only) | Indicates that there is a current but no voltage on L2 (CT/VT only) | [9 empty] | x | [5 empty] | M
225 | E1 | current but no voltage L3 (CT/VT only) | Indicates that there is a current but no voltage on L3 (CT/VT only) | [9 empty] | x | [5 empty] | M
226 | E2 | Billing Profile enabled | Capturing of billing profile has been enabled |  | x | [13 empty] | M
227 | E3 | Billing Profile disabled | Capturing of billing profile has been disabled |  | x | [13 empty] | M
228 | E4 | Display of billing profile enabled | Billing profile 1 values on display enabled |  | x | [13 empty] | M
229 | E5 | Display of billing profile disabled | Billing profile 1 values on display disabled |  | x | [13 empty] | M
230 | E6 | Display of load profile 1 enabled | Load profile 1 values on display enabled |  | x | [13 empty] | M
231 | E7 | Display of load profile 1 disabled | Load profile 1 values on display disabled |  | x | [13 empty] | M
232 | E8 | User text changed | Indicated that the Consumer Message Code - Meter Display value has been successfully changed |  | x | [13 empty] | M
233 | E9 | Local disconnection relay 1 | Indicates that the relay 1 has been locally disconnected (via calendar or limiter threshold). |  |  |  | x | [11 empty] | M | L
234 | EA | Local connection relay 1 | Indicates that the relay 1 has been locally connected (via calendar or limiter threshold). |  |  |  | x | [11 empty] | M | L
235 | EB | Remote disconnection relay 1 | Indicates that the relay 1 has been remotely disconnected. |  |  |  | x | [11 empty] | M | L
236 | EC | Remote connection relay 1 | Indicates that the relay 1 has been remotely connected. |  |  |  | x | [11 empty] | M | L
237 | ED | Local disconnection relay 2 | Indicates that the relay 2 has been locally disconnected (via calendar or limiter threshold). |  |  |  | x | [11 empty] | M | L
238 | EE | Local connection relay 2 | Indicates that the relay 2 has been locally connected (via calendar or limiter threshold). |  |  |  | x | [11 empty] | M | L
239 | EF | Remote disconnection relay 2 | Indicates that the relay 2 has been remotely disconnected. |  |  |  | x | [11 empty] | M | L
240 | F0 | Remote connection relay 2 | Indicates that the relay 2 has been remotely connected. |  |  |  | x | [11 empty] | M | L
241 | F1 | P2P MNO Error | An error code has been received from the Cellular network when communications is attempted. | [10 empty] | x |  |  |  |  | M
242 | F2 | security setup:security_activate method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
243 | F3 | security setup:key_transfer method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
244 | F4 | security setup:key_agreement method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
245 | F5 | security setup:generate_key_pair method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
246 | F6 | security setup:import_certificate method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
247 | F7 | security setup:export_certificate method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
248 | F8 | security setup:remove_certificate method | The method has been successfully operated | [13 empty] | x |  | M |  |  |  |  | 8
249 | F9 | manufacturer specific
250 | FA | manufacturer specific
251 | FB | manufacturer specific
252 | FC | manufacturer specific
253 | FD | manufacturer specific
[5 empty] | x |  |  | x | [9 empty] | M | M
[5 empty] | x | x | x | x | x | x | x | x | x |  |  |  |  | M | M
EOF!
Additional requirements.
|  | Extra events | 1) the certification log shall not be erased or over-writen
2) the security log and fraud detection log shall not be erased or over-written.
Note on S5: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Check that this is in UC20
Note on V75: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Note that L is only a valid option if D is present, therefore not necessary to say D + L
Note on E163: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Is this a duplicate?

## Alarms
Alarm Registers
ALARM REGISTER 3 [0-0:97.98.2.255]
| Bit | Alarm Name | Triggering Event
| 0 | Breaker ready for manual reconnection | 59
| 1 | Manual disconnection breaker | 60
| 2 | Manual connection breaker | 61
| 3 | Remote disconnection breaker | 62
| 4 | Remote connection breaker | 63
| 5 | Local disconnection breaker | 64
| 6 | Local reconnection breaker | 69
| 7 | Limiter 1 import threshold exceeded | 65
| 8 | Limiter 1 import threshold changed | 67
| 9 | Limiter 2 import threshold exceeded | 208
| 10 | Limiter 2 import threshold changed | 210
| 11 | Limiter 1 export threshold exceeded | 213
| 12 | Limiter 1 export threshold changed | 215
| 13 | Limiter 2 export threshold exceeded | 218
| 14 | Limiter 2 export threshold changed | 220
| 15 | Fuse supervision exceeded | 70, 72, 74
| 16 | Customer Interface (H1) state changed | 221, 222
| 17 | Current but no voltage L1-L3 (CT/VT only) | 223, 224, 225
| 18 | User text changed | 232
| 19 | Local disconnection relay 1 | 233
| 20 | Local connection relay 1 | 234
| 21 | Remote disconnection relay 1 | 235
| 22 | Remote connection relay 1 | 236
| 23 | Local disconnection relay 2 | 237
| 24 | Local connection relay 2 | 238
| 25 | Remote disconnection relay 2 | 239
| 26 | Remote connection relay 2 | 240
| 27 | Reserved for future use | -
| 28 | Reserved for future use | -
| 29 | Reserved for future use | -
| 30 | Reserved for future use | -
| 31 | Reserved for future use | -
[1] Any of the listed events shall trigger the alarm.
Note on C22: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: To discuss
Note on D36: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: 2 events for LR FW update

## Display&CII_Lists
Manual Display Requence |  |  |  |  | Automatic Display sequence |  |  |  |  | Profiles Display sequence |  |  |  |  | CII output sequence
Array[1..50]{capture_object_definition} //Selection from the liRt below |  |  |  |  | Array[1..50]{capture_object_definition} /Selection from the list below |  |  |  |  | Array[1..15]{capture_object_definition} /Selection from the list below |  |  |  |  | Array[1..x]](capture_object_definition) //Selection from the list below
|  | result | {2,{3,1-0:1.8.0.255,2,0},{3,1-0:2.8.0.255,2,0},{3,1-0:3.8.0.255,2,0},{3,1-0:4.8.0.255,2,0},{3,1-0:5.8.0.255,2,0},{3,1-0:6.8.0.255,2,0},{3,1-0:7.8.0.255,2,0},{3,1-0:8.8.0.255,2,0},{3,1-0:1.7.0.255,2,0},{3,1-0:2.7.0.255,2,0},{3,1-0:1.6.0.255,2,0},{3,1-0:1.6.0.255,5,0},{3,1-0:2.6.0.255,2,0},{3,1-0:2.6.0.255,5,0},{1,1-0:0.9.1.255,2,0},{1,1-0:0.9.2.255,2,0},{1,0-0:97.97.0.255,2,0},{1,0-0:97.98.0.255,2,0},{1,1-0:0.2.0.255,2,0},{1,1-0:0.2.8.255,2,0},{1,1-1:0.2.0.255,2,0},{1,1-1:0.2.8.255,2,0}}; |  |  |  | result | {2,{3,1-0:1.8.0.255,2,0},{3,1-0:2.8.0.255,2,0},{1,1-0:0.9.1.255,2,0},{1,1-0:0.9.2.255,2,0},{1,0-0:97.97.0.255,2,0},{1,0-0:97.98.0.255,2,0},}; |  |  |  | result | {2,{7,1-0:96.10.1.255,2,0},{7,0-0:98.1.0.255,2,0},{7,1-0:96.10.2.255,2,0},}; |  |  |  |  | results | {2,{1,0-0:96.1.0.255,2,0},{8,0-0:1.0.0.255,2,0},{3,1-0:1.7.0.255,2,0},{3,1-0:2.7.0.255,2,0},{3,1-0:1.8.0.255,2,0},{3,1-0:2.8.0.255,2,0},{3,1-0:3.8.0.255,2,0},{3,1-0:4.8.0.255,2,0},{3,1-0:5.8.0.255,2,0},{3,1-0:6.8.0.255,2,0},{3,1-0:7.8.0.255,2,0},{3,1-0:8.8.0.255,2,0},{3,1-0:32.7.0.255,2,0},{3,1-0:31.7.0.255,2,0},{70,0-1:96.3.10.255,2,0},{70,0-2:96.3.10.255,2,0}}; | {2,{1,0-0:96.1.0.255,2,0},{8,0-0:1.0.0.255,2,0},{3,1-0:1.7.0.255,2,0},{3,1-0:2.7.0.255,2,0},{3,1-0:1.8.0.255,2,0},{3,1-0:2.8.0.255,2,0},{3,1-0:3.8.0.255,2,0},{3,1-0:4.8.0.255,2,0},{3,1-0:5.8.0.255,2,0},{3,1-0:6.8.0.255,2,0},{3,1-0:7.8.0.255,2,0},{3,1-0:8.8.0.255,2,0},{3,1-0:32.7.0.255,2,0},{3,1-0:52.7.0.255,2,0},{3,1-0:72.7.0.255,2,0},{3,1-0:31.7.0.255,2,0},{3,1-0:51.7.0.255,2,0},{3,1-0:71.7.0.255,2,0},{70,0-1:96.3.10.255,2,0},{70,0-2:96.3.10.255,2,0}};
IC | OBIS | Attribute | def | Selected? | IC | OBIS | Attribute | def | Selected? | IC | OBIS | Attribute | def | Selected? | IC | OBIS | Attribute | def | 1 phase | 3 phase
3 | 1-0:1.8.0.255 | 2 | {3,1-0:1.8.0.255,2,0} | TRUE | 3 | 1-0:1.8.0.255 | 2 | {3,1-0:1.8.0.255,2,0} | TRUE | 7 | 1-0:96.10.1.255 | 2 | {7,1-0:96.10.1.255,2,0} | TRUE | 1 | 0-0:96.1.0.255 | 2 | {1,0-0:96.1.0.255,2,0} | TRUE | TRUE
3 | 1-0:2.8.0.255 | 2 | {3,1-0:2.8.0.255,2,0} | TRUE | 3 | 1-0:2.8.0.255 | 2 | {3,1-0:2.8.0.255,2,0} | TRUE | 7 | 0-0:98.1.0.255 | 2 | {7,0-0:98.1.0.255,2,0} | TRUE | 8 | 0-0:1.0.0.255 | 2 | {8,0-0:1.0.0.255,2,0} |  | TRUE
3 | 1-0:3.8.0.255 | 2 | {3,1-0:3.8.0.255,2,0} | TRUE | 3 | 1-0:3.8.0.255 | 2 | {3,1-0:3.8.0.255,2,0} |  | 7 | 1-0:96.10.2.255 | 2 | {7,1-0:96.10.2.255,2,0} | TRUE |  | (add the 1.6.0 & 2.6.0 with time and value)
3 | 1-0:4.8.0.255 | 2 | {3,1-0:4.8.0.255,2,0} | TRUE | 3 | 1-0:4.8.0.255 | 2 | {3,1-0:4.8.0.255,2,0} |  |  |  |  | ?? |  | 4? | 1-0:1.6.0.255 | 2 | ?? | TRUE | TRUE
3 | 1-0:5.8.0.255 | 2 | {3,1-0:5.8.0.255,2,0} | TRUE | 3 | 1-0:5.8.0.255 | 2 | {3,1-0:5.8.0.255,2,0} |  |  |  |  | ?? |  |  | 1-0:1.6.0.255 | 5 | ?? | TRUE | TRUE
3 | 1-0:6.8.0.255 | 2 | {3,1-0:6.8.0.255,2,0} | TRUE | 3 | 1-0:6.8.0.255 | 2 | {3,1-0:6.8.0.255,2,0} |  |  |  |  | ?? |  | 4? | 1-0:2.6.0.255 | 2 | ?? | TRUE | TRUE
3 | 1-0:7.8.0.255 | 2 | {3,1-0:7.8.0.255,2,0} | TRUE | 3 | 1-0:7.8.0.255 | 2 | {3,1-0:7.8.0.255,2,0} |  |  |  |  | ?? |  |  | 1-0:2.6.0.255 | 5 | ?? | TRUE | TRUE
3 | 1-0:8.8.0.255 | 2 | {3,1-0:8.8.0.255,2,0} | TRUE | 3 | 1-0:8.8.0.255 | 2 | {3,1-0:8.8.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:1.7.0.255 | 2 | {3,1-0:1.7.0.255,2,0} | TRUE | TRUE
3 | 1-0:1.7.0.255 | 2 | {3,1-0:1.7.0.255,2,0} | TRUE | 3 | 1-0:1.7.0.255 | 2 | {3,1-0:1.7.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:2.7.0.255 | 2 | {3,1-0:2.7.0.255,2,0} | TRUE | TRUE
3 | 1-0:2.7.0.255 | 2 | {3,1-0:2.7.0.255,2,0} | TRUE | 3 | 1-0:2.7.0.255 | 2 | {3,1-0:2.7.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:3.7.0.255 | 2 | {3,1-0:3.7.0.255,2,0} | TRUE | TRUE
3 | 1-0:1.6.0.255 | 2 | {3,1-0:1.6.0.255,2,0} | TRUE | 3 | 1-0:1.6.0.255 | 2 | {3,1-0:1.6.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:4.7.0.255 | 2 | {3,1-0:4.7.0.255,2,0} | TRUE | TRUE
3 | 1-0:1.6.0.255 | 5 | {3,1-0:1.6.0.255,5,0} | TRUE | 3 | 1-0:1.6.0.255 | 5 | {3,1-0:1.6.0.255,5,0} |  |  |  |  | ?? |  | 3 | 1-0:5.7.0.255 | 2 | {3,1-0:5.7.0.255,2,0} | TRUE | TRUE
3 | 1-0:2.6.0.255 | 2 | {3,1-0:2.6.0.255,2,0} | TRUE | 3 | 1-0:2.6.0.255 | 2 | {3,1-0:2.6.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:6.7.0.255 | 2 | {3,1-0:6.7.0.255,2,0} | TRUE | TRUE
3 | 1-0:2.6.0.255 | 5 | {3,1-0:2.6.0.255,5,0} | TRUE | 3 | 1-0:2.6.0.255 | 5 | {3,1-0:2.6.0.255,5,0} |  |  |  |  | ?? |  | 3 | 1-0:7.7.0.255 | 2 | {3,1-0:7.7.0.255,2,0} | TRUE | TRUE
1 | 1-0:0.9.1.255 | 2 | {1,1-0:0.9.1.255,2,0} | TRUE | 1 | 1-0:0.9.1.255 | 2 | {1,1-0:0.9.1.255,2,0} | TRUE |  |  |  | ?? |  | 3 | 1-0:8.7.0.255 | 2 | {3,1-0:8.7.0.255,2,0} | TRUE | TRUE
1 | 1-0:0.9.2.255 | 2 | {1,1-0:0.9.2.255,2,0} | TRUE | 1 | 1-0:0.9.2.255 | 2 | {1,1-0:0.9.2.255,2,0} | TRUE |  |  |  | ?? |  | 3 | 1-0:1.8.0.255 | 2 | {3,1-0:1.8.0.255,2,0} | TRUE | TRUE
1 | 0-0:97.97.0.255 | 2 | {1,0-0:97.97.0.255,2,0} | TRUE | 1 | 0-0:97.97.0.255 | 2 | {1,0-0:97.97.0.255,2,0} | TRUE |  |  |  | ?? |  | 3 | 1-0:2.8.0.255 | 2 | {3,1-0:2.8.0.255,2,0} | TRUE | TRUE
1 | 0-0:97.98.0.255 | 2 | {1,0-0:97.98.0.255,2,0} | TRUE | 1 | 0-0:97.98.0.255 | 2 | {1,0-0:97.98.0.255,2,0} | TRUE |  |  |  | ?? |  | 3 | 1-0:3.8.0.255 | 2 | {3,1-0:3.8.0.255,2,0} | TRUE | TRUE
1 | 1-0:0.2.0.255 | 2 | {1,1-0:0.2.0.255,2,0} | TRUE | 1 | 1-0:0.2.0.255 | 2 | {1,1-0:0.2.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:4.8.0.255 | 2 | {3,1-0:4.8.0.255,2,0} | TRUE | TRUE
1 | 1-0:0.2.8.255 | 2 | {1,1-0:0.2.8.255,2,0} | TRUE | 1 | 1-0:0.2.8.255 | 2 | {1,1-0:0.2.8.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:5.8.0.255 | 2 | {3,1-0:5.8.0.255,2,0} | TRUE | TRUE
1 | 1-1:0.2.0.255 | 2 | {1,1-1:0.2.0.255,2,0} | TRUE | 1 | 1-1:0.2.0.255 | 2 | {1,1-1:0.2.0.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:6.8.0.255 | 2 | {3,1-0:6.8.0.255,2,0} | TRUE | TRUE
1 | 1-1:0.2.8.255 | 2 | {1,1-1:0.2.8.255,2,0} | TRUE | 1 | 1-1:0.2.8.255 | 2 | {1,1-1:0.2.8.255,2,0} |  |  |  |  | ?? |  | 3 | 1-0:7.8.0.255 | 2 | {3,1-0:7.8.0.255,2,0} | TRUE | TRUE
[15 empty] | 3 | 1-0:8.8.0.255 | 2 | {3,1-0:8.8.0.255,2,0} | TRUE | TRUE
[15 empty] | 3 | 1-0:32.7.0.255 | 2 | {3,1-0:32.7.0.255,2,0} | TRUE | TRUE
[15 empty] | 3 | 1-0:52.7.0.255 | 2 | {3,1-0:52.7.0.255,2,0} |  | TRUE
[15 empty] | 3 | 1-0:72.7.0.255 | 2 | {3,1-0:72.7.0.255,2,0} |  | TRUE
[15 empty] | 3 | 1-0:31.7.0.255 | 2 | {3,1-0:31.7.0.255,2,0} | TRUE | TRUE
[15 empty] | 3 | 1-0:51.7.0.255 | 2 | {3,1-0:51.7.0.255,2,0} |  | TRUE
[15 empty] | 3 | 1-0:71.7.0.255 | 2 | {3,1-0:71.7.0.255,2,0} |  | TRUE
[15 empty] | 70 | 0-1:96.3.10.255 | 2 | {70,0-1:96.3.10.255,2,0} | TRUE | TRUE
[15 empty] | 70 | 0-2:96.3.10.255 | 2 | {70,0-2:96.3.10.255,2,0} | TRUE | TRUE
Note, values in italics are not mandatory accoridng to the law

## Ethernet object structures
Ethernet Object Structures
Ethernet configuration
MTU | long-unsigned | Default: 1280
Speed | enum | enum:
(0)AUTO
(1)10M
(2)100M
(3)1G
DuplexMode | enum | enum:
(0)AUTO
(1)FullDuplex
(2)HalfDuplex
VLANID | long-unsigned | Default: 1
Status_LED | enum | enum:
(0)LED disabled
(1)LED enabled
Ethernet_Enabled | enum | enum:
(0)Port disabled
(1)Port enabled
Ethernet filter
Drop_Multicast | enum | enum:
(0)disabled
(1)enabled
Drop_Broadcast | enum | enum:
(0)disabled
(1)enabled
Drop_DHCP_req | enum | enum:
(0)disabled
(1)enabled
Drop_ARP | enum | enum:
(0)disabled
(1)enabled
ACL_MAC | structure | List of allowed MAC_Addresses:
Value ::= structure
{
MAC1,
MAC2,
MAC3,
…...
}
ACL_IP | structure | List of allowed IP_Subnet:
Value ::= structure
{
IP_Subnet1,
IP_Subnet1,
IP_Subnet1,
…...
}
Ethernet Status
Ethernet_status | enum | enum:
(0)Port DOWN
(1)Port UP
Speed | enum | enum:
(0)10M
(1)100M
(2)1G
Duplexmode | enum | enum:
(0)FullDuplex
(1)HalfDuplex
Note. All other enum values are reserved.

## Push objects (hidden)
PUSH Objects
Objects concerning Push
# | Object / Attribute Name | Supported Objects |  | IC |  | Default Value
|  | 102 | 103 | Class | Ver.
| Push setup - Interval_1 | M | M | 40 | 0 | 0-1:25.9.0.255
| Push setup - Interval_2 | M | M | 40 | 0 | 0-2:25.9.0.255
| Push setup - Interval_3 | M | M | 40 | 0 | 0-3:25.9.0.255
| Push setup - On Power down | M | M | 40 | 0 | 0-5:25.9.0.255
| Push action scheduler - Interval_1 | M | M | 22 | 0 | 0-1:15.0.4.255
| Push action scheduler - Interval_2 | M | M | 22 | 0 | 0-2:15.0.4.255
| Push action scheduler - Interval_3 | M | M | 22 | 0 | 0-3:15.0.4.255
# | Object / Attribute Name | Supported Objects |  | IC |  | Default Value
|  | 102 | 103 | Class | Ver.
| Push setup - Customer Information | O | O | 40 | 0 | 0-6:25.9.0.255
| Push action scheduler - Customer Information | O | O | 22 | 0 | 0-4:15.0.4.255
| Security setup - Customer Information | O | O | 64 | 0 | 0-0:43.0.1.255
| IEC HDLC setup - Consumer Information port | O | O | 23 | 1 | 0-1:22.0.0.255
M=mandatory, O=optional, NA=not applicable